## Front page
Project
Project number: | 1 | Project version:
Description: | Sample project of ceiling heating/cooling system
Street: | Zjednoczenia 2
Postal code and city: | Chorzów | Telephone: | (+48) 32 750 52 01
Country: | Poland | Fax:
WWW: | www.instalsoft.com
E-mail: | info@instalsoft.com.pl
Comment
Project developer
Name: | InstalSoft s.c.
Street:
Postal code and city: |  | Telephone:
Country: |  | Fax:
WWW:
E-mail:
VAT-id:
Comment
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  | - 1 -
Designer
Name: | InstalSoft s.c.
Street:
Postal code and city: |  | Telephone:
Country: |  | Fax:
WWW:
E-mail:
VAT-id:
Comment
File info
File name: | C:\Users\staneka.INSTALSOFT\Downloads\Installation-cooling-ceiling-system-in-commercial-building(3).isproj
Program version: | 5.0 (Rev. 15.9.2)
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  | - 2 -

## General results heating
Project: Sample project of ceiling heating/cooling system
General results heating
No. of sources |  |  | 1
Total number of terminal units |  |  | 17
Total number of pipe-runs |  |  | 30
Total number of manifolds |  |  | 4
Total number of pumps |  |  | 0
Spec. total rooms heat loss ΦH |  |  | 20687 |  | W
Spec. total req. heat output of other TU's |  |  | 0 |  | W
Spec. total rooms req. heat output Φreq |  |  | 20687 |  | W
Calculation standards:
Radiators sizing standard |  |  | EN 442-2
Floor heating standard |  |  | EN 1264-1,2,3:1999, EN 1264-4:2003
Source: Other (hor.): 1, Application: Heating engineering/Refrigerating engineering, Medium: Water
| Source elevation |  | -2.8 |  | m
| Supply and return temperature |  | 40,8 / 28,0 |  | °C
| Total output |  | 19251 |  | W
| Total output of convectors Φconv,H |  | 0 |  | W
| Total output of radiant heaters Φrh,H |  | 16500 |  | W
| Total output of other heaters |  | 0 |  | W
| Heat gains from pipe-runs accounted for in balance |  | 0 |  | W
| Not utilized heat loss of pipe-runs |  | 258 |  | W
| Losses of radiant heating (outside building) |  | 2492 |  | W
| Losses of radiant heating (inside buidling) |  | 0 |  | W
| Available pressure |  | 54.6 |  | kPa
| Pressure drop along critical route |  | 54.6 |  | kPa
| Pressure drop on critical terminal unit |  | 11.7 |  | kPa
| Press. drop on source |  | 0 |  | kPa
| Flow rate in source |  | 1293.6 |  | kg/h
| Critical receptor: | 0,8-4-4
| Critical TU route length |  | 79.7 |  | m
| Capacity of system incl. terminal units |  | 226.8 |  | dm³
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  | - 3 -

## Radiant heating general res
Project: Sample project of ceiling heating/cooling system
Radiant heating general results
Source/Source: 1 |  |  |  | Application: Heating engineering/Refrigerating engineering | [6 empty] | Medium: Water
Temperatures θs,H and θr,H [°C] |  |  | 40.8 |  |  |  | 28
Temperature source for control circuits |  | Source/1
Temperatures θs,H and θr,H [°C] |  |  | 40.8 |  |  |  | 28
Required heat capacity Φreq,H [W] |  |  | 16500
Obtained heat output ΦH [W] |  |  | 16500
Heat capacity lost ΦDS,H [W] |  |  | 2492
Mass flow rate m [kg/h] |  |  | 1293.6
Manifold symbol | Storey symbol |  | Number of heating/cooling zones fed |  | Obtained heat output of heat./cool. zone (heating mode) | Output lost of heat./cool. zone (heating mode) |  | Return temperature on manifold (heating mode) | Temperature difference on manifold (heating mode) | Mass flow rate |  | Required min. pressure difference | Resultant pressure difference | Total pipe length
Manifold | Stor. |  | N |  | ΦH | ΦDS,H |  | θr,H | ΔθH | m |  | Δpmin | Δp | Ltot
[5 empty] | W | W |  | °C | K | kg/h |  | kPa | kPa | m
M1 | 2 |  | 6 |  | 5556 | 849 |  | 27.5 | 13.2 | 417.9 |  | 7.6 | 15 | 610,1
M2 | 2 |  | 5 |  | 5540 | 846 |  | 27.5 | 13.1 | 419.2 |  | 13.1 | 13.1 | 592,2
M3 | 2 |  | 3 |  | 2895 | 427 |  | 28.8 | 11.9 | 239.8 |  | 9.2 | 10.4 | 266,4
M4 | 2 |  | 3 |  | 2509 | 370 |  | 29.1 | 11.5 | 216.7 |  | 9.1 | 9.1 | 238,3
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [12 empty] | - 4 -

## Radiant cooling general res
Project: Sample project of ceiling heating/cooling system
Radiant cooling general results
Source/Source: 1 |  |  |  | Application: Heating engineering/Refrigerating engineering | [6 empty] | Medium: Water
Temperatures θs,C and θr,C [°C] |  |  | 17 |  |  |  | ???
Temperature source for control circuits |  | Source/1
Temperatures θs,C and θr,C [°C] |  |  | 17 |  |  |  | ???
Required heat capacity Φreq,C [W] |  |  | 13500
Obtained heat output ΦC [W] |  |  | 8574
Heat capacity lost ΦDS,C [W] |  |  | 112
Mass flow rate m [kg/h] |  |  | 1293.6
Manifold symbol | Storey symbol |  | Number of heating/cooling zones fed |  | Obtained heat output of heat./cool. zone (cooling mode) | Output lost of heat./cool. zone (cooling mode) |  | Return temperature on manifold (cooling mode) | Temperature difference on manifold (cooling mode) | Mass flow rate |  | Required min. pressure difference |  | Resultant pressure difference | Total pipe length
Manifold | Stor. |  | N |  | ΦC | ΦDS,C |  | θr,C | ΔθC | m |  | Δpmin |  | Δp | Ltot
[5 empty] | W | W |  | °C | K | kg/h |  | kPa |  | kPa | m
M1 | 2 |  | 6 |  | 2890 | 41 |  | 22.9 | -5.9 | 417.9 |  | 7.6 |  | 15 | 610,1
M2 | 2 |  | 5 |  | 2882 | 41 |  | 22.9 | -5.9 | 419.2 |  | 13.1 |  | 13.1 | 592,2
M3 | 2 |  | 3 |  | 1501 | 16 |  | 22.4 | -5.4 | 239.8 |  | 9.2 |  | 10.4 | 266,4
M4 | 2 |  | 3 |  | 1301 | 14 |  | 22.2 | -5.2 | 216.7 |  | 9.1 |  | 9.1 | 238,3
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [12 empty] | - 5 -

## Detailed radiant heating re
Project: Sample project of ceiling heating/cooling system
Detailed radiant heating results
Heating/cooling zone symbol |  | Area | Occupied / peripheral zone | Surface temperature |  | Thermal resistance of covering |  | Power required for heating |  | Output gained |  | Output lost |  | Unit power |  | Pipe spacing |  | Temp. diff. supply-return |  | Area occupied by passing feeds |  | Heating power from passing feeds |  | Length of circuit feeds |  | Overall circuit length (feeds + loop) |  | Mass flow rate |  | Flow velocity |  | Pressure loss in circuit |  | Pressure drop on regulating valves |  | Total pressure loss |  |  | Valve setting
HCZ |  | A | Type | θsurface,H |  | Rλ,B |  | Φreq,H |  | ΦH |  | ΦDS,H |  | qH |  | VA |  | ΔθH |  | Afeed |  | Φfeeds,H |  | Lfeeds |  | Ltot |  | m |  | v |  | Δp |  | Δpreg,z Δpreg,p |  | Δptot |  |  | n
|  | m² |  | °C |  | (m²·K)/W |  | W |  | W |  | W |  | W/m² |  | mm |  | K |  | m² |  | W |  | m |  | m |  | kg/h |  | m/s |  | kPa |  | kPa |  | kPa
Double apartment manifold: M1; Storey: 2; Bld. unit: NONE; θs,H: 40,8 °C;
Room: 0,8; θi,H: 20,0 °C; Φreq,H: 11096 W; Φ surplus: 0 W;
| 0,8-1-1 | 17.7 | OZ | 28.5 | 0 |  | 973 |  | 973 |  | 149 |  | 55 |  | 200 |  | 13.2 |  | 0 |  | 0 |  | 5.7 |  | 94.2 |  | 73.1 |  | 0.18 |  | 5.2 |  | 6,4 3,4 |  | 15 |  |  | 3,00
| 0,8-1-2 | 17.7 | OZ | 28.5 | 0 |  | 973 |  | 973 |  | 149 |  | 55 |  | 200 |  | 13.2 |  | 0 |  | 0 |  | 11.8 |  | 100.2 |  | 73.1 |  | 0.18 |  | 5.6 |  | 6,4 3,0 |  | 15 |  |  | 3,00
| 0,8-1-3 | 17.7 | OZ | 28.5 | 0 |  | 973 |  | 973 |  | 149 |  | 55 |  | 200 |  | 13.2 |  | 0 |  | 0 |  | 18.1 |  | 106.6 |  | 73.1 |  | 0.18 |  | 5.9 |  | 6,4 2,7 |  | 15 |  |  | 3,00
| 0,8-1-4 | 17.7 | OZ | 28.5 | 0 |  | 973 |  | 973 |  | 149 |  | 55 |  | 200 |  | 13.2 |  | 0 |  | 0 |  | 24.2 |  | 112.6 |  | 73.1 |  | 0.18 |  | 6.3 |  | 6,4 2,3 |  | 15 |  |  | 3,00
| 0,8-1-5 | 17.7 | OZ | 28.5 | 0 |  | 973 |  | 973 |  | 149 |  | 55 |  | 200 |  | 13.2 |  | 0 |  | 0 |  | 30.5 |  | 118.9 |  | 73.1 |  | 0.18 |  | 6.6 |  | 6,4 2,0 |  | 15 |  |  | 3,00
| 0,8-2-1 | 12.6 | OZ | 28.5 | 0 |  | 692 |  | 692 |  | 106 |  | 55 |  | 200 |  | 13.1 |  | 0 |  | 0 |  | 14.7 |  | 77.6 |  | 52.4 |  | 0.13 |  | 1.6 |  | 11,0 2,4 |  | 15 |  |  | 1,50
Double apartment manifold: M2; Storey: 2; Bld. unit: NONE; θs,H: 40,8 °C;
Room: 0,8; θi,H: 20,0 °C; Φreq,H: 11096 W; Φ surplus: 0 W;
| 0,8-3-1 | 12.5 | OZ | 28.5 | 0 |  | 686 |  | 686 |  | 105 |  | 55 |  | 200 |  | 13.1 |  | 0 |  | 0 |  | 13.2 |  | 75.6 |  | 51.9 |  | 0.13 |  | 1.6 |  | 10,8 0,8 |  | 13.1 |  |  | 1,50
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [36 empty] | - 6 -
Project: Sample project of ceiling heating/cooling system
HCZ |  | A | Type | θsurface,H |  | Rλ,B |  | Φreq,H |  | ΦH |  | ΦDS,H |  | qH |  | VA |  | ΔθH |  | Afeed |  | Φfeeds,H |  | Lfeeds |  | Ltot |  | m |  | v |  | Δp |  | Δpreg,z Δpreg,p |  | Δptot |  |  | n
|  | m² |  | °C |  | (m²·K)/W |  | W |  | W |  | W |  | W/m² |  | mm |  | K |  | m² |  | W |  | m |  | m |  | kg/h |  | m/s |  | kPa |  | kPa |  | kPa
| 0,8-4-1 | 22.1 | OZ | 28.5 | 0 |  | 1214 |  | 1214 |  | 185 |  | 55 |  | 200 |  | 13.1 |  | 0 |  | 0 |  | 7.1 |  | 117.5 |  | 91.8 |  | 0.23 |  | 9.7 |  | 2,7 0,7 |  | 13.1 |  |  | 5,00
| 0,8-4-2 | 22.1 | OZ | 28.5 | 0 |  | 1214 |  | 1214 |  | 185 |  | 55 |  | 200 |  | 13.1 |  | 0 |  | 0 |  | 14.9 |  | 125.2 |  | 91.8 |  | 0.23 |  | 10.4 |  | 2,2 0,6 |  | 13.1 |  |  | 5,50
| 0,8-4-3 | 22.1 | OZ | 28.5 | 0 |  | 1214 |  | 1214 |  | 185 |  | 55 |  | 200 |  | 13.1 |  | 0 |  | 0 |  | 22.7 |  | 133.1 |  | 91.8 |  | 0.23 |  | 11 |  | 1,4 0,7 |  | 13.1 |  |  | 6,50
| 0,8-4-4 | 22.1 | OZ | 28.5 | 0 |  | 1214 |  | 1214 |  | 185 |  | 55 |  | 200 |  | 13.1 |  | 0 |  | 0 |  | 30.5 |  | 140.8 |  | 91.8 |  | 0.23 |  | 11.7 |  | 0,9 0,6 |  | 13.1 |  |  | 8,00
Double apartment manifold: M3; Storey: 2; Bld. unit: NONE; θs,H: 40,8 °C;
Room: 0,1; θi,H: 20,0 °C; Φreq,H: 5404 W; Φ surplus: 0 W;
| 0,1-1-1 | 18.3 | OZ | 29 | 0 |  | 1077 |  | 1077 |  | 159 |  | 58.7 |  | 200 |  | 12 |  | 0 |  | 0 |  | 8.7 |  | 100.5 |  | 89 |  | 0.22 |  | 7.8 |  | 2,0 0,6 |  | 10.4 |  |  | 5,50
| 0,1-1-2 | 18.3 | OZ | 29 | 0 |  | 1077 |  | 1077 |  | 159 |  | 58.7 |  | 200 |  | 12 |  | 0 |  | 0 |  | 2.8 |  | 94.5 |  | 89 |  | 0.22 |  | 7.4 |  | 2,0 1,0 |  | 10.4 |  |  | 5,50
| 0,1-2-1 | 12.6 | OZ | 29 | 0 |  | 740 |  | 740 |  | 109 |  | 58.7 |  | 200 |  | 11.8 |  | 0 |  | 0 |  | 8.4 |  | 71.4 |  | 61.9 |  | 0.15 |  | 3 |  | 6,9 0,5 |  | 10.4 |  |  | 2,50
Double apartment manifold: M4; Storey: 2; Bld. unit: NONE; θs,H: 40,8 °C;
Room: 0,1; θi,H: 20,0 °C; Φreq,H: 5404 W; Φ surplus: 0 W;
| 0,1-3-1 | 6.2 | OZ | 29 | 0 |  | 365 |  | 365 |  | 54 |  | 58.7 |  | 200 |  | 9.1 |  | 0 |  | 0 |  | 13.5 |  | 44.6 |  | 39.7 |  | 0.1 |  | 0.7 |  | 6,3 2,1 |  | 9.1 |  |  | 1,50
| 0,1-4-1 | 18.3 | OZ | 29 | 0 |  | 1072 |  | 1072 |  | 158 |  | 58.7 |  | 200 |  | 12 |  | 0 |  | 0 |  | 8.4 |  | 99.7 |  | 88.5 |  | 0.22 |  | 7.7 |  | 0,8 0,5 |  | 9.1 |  |  | 8,00
| 0,1-4-2 | 18.3 | OZ | 29 | 0 |  | 1072 |  | 1072 |  | 158 |  | 58.7 |  | 200 |  | 12 |  | 0 |  | 0 |  | 2.8 |  | 94.1 |  | 88.5 |  | 0.22 |  | 7.3 |  | 1,0 0,8 |  | 9.1 |  |  | 7,00
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [36 empty] | - 7 -

## Detailed radiant cooling re
Project: Sample project of ceiling heating/cooling system
Detailed radiant cooling results
Heating/cooling zone symbol |  |  | Area |  |  | Occupied / peripheral zone | Surface temperature |  | Thermal resistance of covering |  | Power required for cooling |  | Power gained | Output lost |  | Unit power | Pipe spacing | Temp. diff. supply-return | Area occupied by passing feeds | Cooling output of passing pipe feeds | Length of circuit feeds | Overall circuit length (feeds + loop) | Mass flow rate | Flow velocity | Pressure loss in circuit | Pressure drop on regulating valves | Total pressure loss |  | Valve setting
HCZ |  |  | A |  |  | Type | θsurface,C |  | Rλ,B |  | Φreq,C |  | ΦC | ΦDS,C |  | qC | VA | ΔθC | Afeed | Φfeeds,C | Lfeeds | Ltot | m | v | Δp | Δpreg,z Δpreg,p | Δptot |  | n
|  |  | m² |  |  |  | °C |  | (m²·K)/W |  | W |  | W | W |  | W/m² | mm | K | m² | W | m | m | kg/h | m/s | kPa | kPa | kPa
Double apartment manifold: M1; Storey: 2; Bld. unit: NONE; θs,C: 17,0 °C;
| Room: | 0,8; |  | θi,C: | 26,0 °C; |  |  | Φreq,C: |  | 9079 W; |  | Φ surplus,C: |  |  | -3307 W;
| 0,8-1-1 |  | 17.7 |  |  | OZ | 23.4 |  | 0,000 |  | 796 |  | 506 | 7 |  | 28.6 | 200 | -5.9 | 0 | 0 | 5.7 | 94.2 | 73.1 | 0.18 | 5.2 | 6,4 3,4 | 15 |  | 3
| 0,8-1-2 |  | 17.7 |  |  | OZ | 23.4 |  | 0,000 |  | 796 |  | 506 | 7 |  | 28.6 | 200 | -5.9 | 0 | 0 | 11.8 | 100.2 | 73.1 | 0.18 | 5.6 | 6,4 3,0 | 15 |  | 3
| 0,8-1-3 |  | 17.7 |  |  | OZ | 23.4 |  | 0,000 |  | 796 |  | 506 | 7 |  | 28.6 | 200 | -5.9 | 0 | 0 | 18.1 | 106.6 | 73.1 | 0.18 | 5.9 | 6,4 2,7 | 15 |  | 3
| 0,8-1-4 |  | 17.7 |  |  | OZ | 23.4 |  | 0,000 |  | 796 |  | 506 | 7 |  | 28.6 | 200 | -5.9 | 0 | 0 | 24.2 | 112.6 | 73.1 | 0.18 | 6.3 | 6,4 2,3 | 15 |  | 3
| 0,8-1-5 |  | 17.7 |  |  | OZ | 23.4 |  | 0,000 |  | 796 |  | 506 | 7 |  | 28.6 | 200 | -5.9 | 0 | 0 | 30.5 | 118.9 | 73.1 | 0.18 | 6.6 | 6,4 2,0 | 15 |  | 3
| 0,8-2-1 |  | 12.6 |  |  | OZ | 23.4 |  | 0,000 |  | 566 |  | 360 | 5 |  | 28.6 | 200 | -5.9 | 0 | 0 | 14.7 | 77.6 | 52.4 | 0.13 | 1.6 | 11,0 2,4 | 15 |  | 1.5
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [27 empty] | - 8 -
Project: Sample project of ceiling heating/cooling system
HCZ |  |  | A |  |  | Type | θsurface,C |  | Rλ,B |  | Φreq,C |  | ΦC | ΦDS,C |  | qC | VA | ΔθC | Afeed | Φfeeds,C | Lfeeds | Ltot | m | v | Δp | Δpreg,z Δpreg,p | Δptot |  | n
|  |  | m² |  |  |  | °C |  | (m²·K)/W |  | W |  | W | W |  | W/m² | mm | K | m² | W | m | m | kg/h | m/s | kPa | kPa | kPa
Double apartment manifold: M2; Storey: 2; Bld. unit: NONE; θs,C: 17,0 °C;
| Room: | 0,8; |  | θi,C: | 26,0 °C; |  |  | Φreq,C: |  | 9079 W; |  | Φ surplus,C: |  |  | -3307 W;
| 0,8-3-1 |  | 12.5 |  |  | OZ | 23.4 |  | 0,000 |  | 561 |  | 357 | 5 |  | 28.6 | 200 | -5.9 | 0 | 0 | 13.2 | 75.6 | 51.9 | 0.13 | 1.6 | 10,8 0,8 | 13.1 |  | 1.5
| 0,8-4-1 |  | 22.1 |  |  | OZ | 23.4 |  | 0,000 |  | 993 |  | 631 | 9 |  | 28.6 | 200 | -5.9 | 0 | 0 | 7.1 | 117.5 | 91.8 | 0.23 | 9.7 | 2,7 0,7 | 13.1 |  | 5
| 0,8-4-2 |  | 22.1 |  |  | OZ | 23.4 |  | 0,000 |  | 993 |  | 631 | 9 |  | 28.6 | 200 | -5.9 | 0 | 0 | 14.9 | 125.2 | 91.8 | 0.23 | 10.4 | 2,2 0,6 | 13.1 |  | 5.5
| 0,8-4-3 |  | 22.1 |  |  | OZ | 23.4 |  | 0,000 |  | 993 |  | 631 | 9 |  | 28.6 | 200 | -5.9 | 0 | 0 | 22.7 | 133.1 | 91.8 | 0.23 | 11 | 1,4 0,7 | 13.1 |  | 6.5
| 0,8-4-4 |  | 22.1 |  |  | OZ | 23.4 |  | 0,000 |  | 993 |  | 631 | 9 |  | 28.6 | 200 | -5.9 | 0 | 0 | 30.5 | 140.8 | 91.8 | 0.23 | 11.7 | 0,9 0,6 | 13.1 |  | 8
Double apartment manifold: M3; Storey: 2; Bld. unit: NONE; θs,C: 17,0 °C;
| Room: | 0,1; |  | θi,C: | 26,0 °C; |  |  | Φreq,C: |  | 4421 W; |  | Φ surplus,C: |  |  | -1619 W;
| 0,1-1-1 |  | 18.3 |  |  | OZ | 23.2 |  | 0,000 |  | 881 |  | 559 | 6 |  | 30.5 | 200 | -5.4 | 0 | 0 | 8.7 | 100.5 | 89 | 0.22 | 7.8 | 2,0 0,6 | 10.4 |  | 5.5
| 0,1-1-2 |  | 18.3 |  |  | OZ | 23.2 |  | 0,000 |  | 881 |  | 559 | 6 |  | 30.5 | 200 | -5.4 | 0 | 0 | 2.8 | 94.5 | 89 | 0.22 | 7.4 | 2,0 1,0 | 10.4 |  | 5.5
| 0,1-2-1 |  | 12.6 |  |  | OZ | 23.2 |  | 0,000 |  | 605 |  | 384 | 4 |  | 30.5 | 200 | -5.4 | 0 | 0 | 8.4 | 71.4 | 61.9 | 0.15 | 3 | 6,9 0,5 | 10.4 |  | 2.5
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [27 empty] | - 9 -
Project: Sample project of ceiling heating/cooling system
HCZ |  |  | A |  |  | Type | θsurface,C |  | Rλ,B |  | Φreq,C |  | ΦC | ΦDS,C |  | qC | VA | ΔθC | Afeed | Φfeeds,C | Lfeeds | Ltot | m | v | Δp | Δpreg,z Δpreg,p | Δptot |  | n
|  |  | m² |  |  |  | °C |  | (m²·K)/W |  | W |  | W | W |  | W/m² | mm | K | m² | W | m | m | kg/h | m/s | kPa | kPa | kPa
Double apartment manifold: M4; Storey: 2; Bld. unit: NONE; θs,C: 17,0 °C;
| Room: | 0,1; |  | θi,C: | 26,0 °C; |  |  | Φreq,C: |  | 4421 W; |  | Φ surplus,C: |  |  | -1619 W;
| 0,1-3-1 |  | 6.2 |  |  | OZ | 23.2 |  | 0,000 |  | 299 |  | 189 | 2 |  | 30.4 | 200 | -4.2 | 0 | 0 | 13.5 | 44.6 | 39.7 | 0.1 | 0.7 | 6,3 2,1 | 9.1 |  | 1.5
| 0,1-4-1 |  | 18.3 |  |  | OZ | 23.2 |  | 0,000 |  | 877 |  | 556 | 6 |  | 30.5 | 200 | -5.4 | 0 | 0 | 8.4 | 99.7 | 88.5 | 0.22 | 7.7 | 0,8 0,5 | 9.1 |  | 8
| 0,1-4-2 |  | 18.3 |  |  | OZ | 23.2 |  | 0,000 |  | 877 |  | 556 | 6 |  | 30.5 | 200 | -5.4 | 0 | 0 | 2.8 | 94.1 | 88.5 | 0.22 | 7.3 | 1,0 0,8 | 9.1 |  | 7
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [27 empty] | - 10 -

## List of rooms - heating
Project: Sample project of ceiling heating/cooling system
List of rooms - heating
Room Symbol |  |  |  |  | Room surface area | Thermal resistance of covering |  | Room temperature during heating period | Heat loss in room | Required output of heating function | Required specific output of heating function | Required radiant heating output | Required convection heating output | Obtained radiant heating output | Obtained convection heating output | Output recovered from pipe-runs | Coverage of heat loss in room
Room |  |  |  |  | A | Rλ,B |  | θi,H | Φstd,H | Φreq,H | qreq,H | Φreq,rad,H | Φreq,conv,H | Φrh,H | Φconv,H | Φpipe,H | %Φreq,H
[5 empty] | m² | (m²·K)/W |  | °C | W | W | W/m² | W | W | W | W | W | %
Storey: |  | 1, | Elevation |  |  |  | 0 m
| Bld. unit: |  |  | 01
| (no name) |  |  |  | 5.7 |  |  | 20 | 0 | 315 | 55 | 0 | 315 | 0 | 0 | 0 | 0
| (no name) |  |  |  | 9.5 |  |  | 20 | 0 | 524 | 55 | 0 | 524 | 0 | 0 | 0 | 0
| (no name) |  |  |  | 2.9 |  |  | 20 | 0 | 159 | 55 | 0 | 159 | 0 | 0 | 0 | 0
| (no name) |  |  |  | 9.2 |  |  | 20 | 0 | 504 | 55 | 0 | 504 | 0 | 0 | 0 | 0
| (no name) |  |  |  | 3.3 |  |  | 20 | 0 | 183 | 55 | 0 | 183 | 0 | 0 | 0 | 0
| 0,1 |  |  |  | 98.3 | 0 |  | 20 | 0 | 5404 | 55 | 5404 | 0 | 5404 | 0 | 0 | 100
| 0,2 |  |  |  | 5.7 |  |  | 20 | 0 | 315 | 55 | 0 | 315 | 0 | 0 | 0 | 0
| 0,3 |  |  |  | 2.9 |  |  | 20 | 0 | 159 | 55 | 0 | 159 | 0 | 0 | 0 | 0
| 0,4 |  |  |  | 3.3 |  |  | 20 | 0 | 183 | 55 | 0 | 183 | 0 | 0 | 0 | 0
| 0,5 |  |  |  | 4.3 |  |  | 20 | 0 | 238 | 55 | 0 | 238 | 0 | 0 | 0 | 0
| 0,6 |  |  |  | 29.2 |  |  | 20 | 0 | 1606 | 55 | 0 | 1606 | 0 | 0 | 0 | 0
| 0,8 |  |  |  | 201.8 | 0 |  | 20 | 0 | 11096 | 55 | 11096 | 0 | 11096 | 0 | 0 | 100
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [15 empty] | - 11 -

## List of rooms - cooling
Project: Sample project of ceiling heating/cooling system
List of rooms - cooling
Room Symbol |  |  |  |  | Room surface area |  | Thermal resistance of covering | Room temperature during cooling period | Required output of cooling function | Required specific output of cooling function | Required radiant cooling output | Required convection cooling output |  | Obtained radiant cooling output |  | Obtained convection cooling output |  | Coverage of required cooling output
Room |  |  |  |  | A |  | Rλ,B | θi,C | Φreq,C | qreq,C | Φreq,rad,C | Φreq,conv,C |  | Φrh,C |  | Φconv,C |  | %Φreq,C
[5 empty] | m² |  | (m²·K)/W | °C | W | W/m² | W | W |  | W |  | W |  | %
Storey: |  | 1, | Elevation |  |  | 0 m
| Bld. unit: |  |  | 01
| 0,1 |  |  |  | 98.3 |  | 0 | 26 | 4421 | 45 | 4421 |  | 2802 |  | 0 |  | 63
| 0,8 |  |  |  | 201.8 |  | 0 | 26 | 9079 | 45 | 9079 |  | 5771 |  | 0 |  | 64
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [17 empty] | - 12 -

## Manifold boards
Project: Sample project of ceiling heating/cooling system
Manifold board: M1
Storey: |  |  |  | 2
Building unit: |  |  |  | NONE
Type: |  |  |  | Manifold with balancing screws
Number of outlet pairs: |  |  |  | 6
Manifold set: |  |  |  | With ball valve straight
Manifold cabinet: |  |  |  | Concealed manifold cabinet
No. |  | Type | To terminal unit |  |  | To room | Room label | Pipe type |  | Diameter |  |  | Valve set.
mm
1 |  | Heating/cooling ceiling | 0,8-2-1 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 1.5
2 |  | Heating/cooling ceiling | 0,8-1-5 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 3
3 |  | Heating/cooling ceiling | 0,8-1-4 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 3
4 |  | Heating/cooling ceiling | 0,8-1-3 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 3
5 |  | Heating/cooling ceiling | 0,8-1-2 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 3
6 |  | Heating/cooling ceiling | 0,8-1-1 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 3
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [11 empty] | - 13 -
Project: Sample project of ceiling heating/cooling system
List of radiant heating components
Product |  |  |  |  | Size |  |  |  | Catalogue code |  | Quantity |  |  | Unit
Basic radiant systems
Manifolds
| Manifold with balancing screws |  |  |  | 6 ways |  |  |  | any producer |  | 1 |  |  | pcs.
Manifold cabinets
| Concealed manifold cabinet |  |  |  | 500x750x160 |  |  |  | any producer |  | 1 |  |  | pcs.
Valves
| Straight ball valve 1'' |  |  |  | 25 |  |  |  | any producer |  | 1 |  |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [11 empty] | - 14 -
Project: Sample project of ceiling heating/cooling system
Manifold board: M2
Storey: |  |  |  | 2
Building unit: |  |  |  | NONE
Type: |  |  |  | Manifold with balancing screws
Number of outlet pairs: |  |  |  | 5
Manifold set: |  |  |  | With ball valve straight
Manifold cabinet: |  |  |  | Concealed manifold cabinet
No. |  | Type | To terminal unit |  |  | To room | Room label | Pipe type |  | Diameter |  |  | Valve set.
mm
1 |  | Heating/cooling ceiling | 0,8-3-1 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 1.5
2 |  | Heating/cooling ceiling | 0,8-4-4 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 8
3 |  | Heating/cooling ceiling | 0,8-4-3 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 6.5
4 |  | Heating/cooling ceiling | 0,8-4-2 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 5.5
5 |  | Heating/cooling ceiling | 0,8-4-1 |  |  | 0.8 | Living room | PEX pipe |  | 16x2.0 |  |  | 5
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [11 empty] | - 15 -
Project: Sample project of ceiling heating/cooling system
List of radiant heating components
Product |  |  |  |  | Size |  |  |  | Catalogue code |  | Quantity |  |  | Unit
Basic radiant systems
Manifolds
| Manifold with balancing screws |  |  |  | 5 ways |  |  |  | any producer |  | 1 |  |  | pcs.
Manifold cabinets
| Concealed manifold cabinet |  |  |  | 400x750x160 |  |  |  | any producer |  | 1 |  |  | pcs.
Valves
| Straight ball valve 1'' |  |  |  | 25 |  |  |  | any producer |  | 1 |  |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [11 empty] | - 16 -
Project: Sample project of ceiling heating/cooling system
Manifold board: M3
Storey: |  |  |  | 2
Building unit: |  |  |  | NONE
Type: |  |  |  | Manifold with balancing screws
Number of outlet pairs: |  |  |  | 3
Manifold set: |  |  |  | With ball valve straight
Manifold cabinet: |  |  |  | Concealed manifold cabinet
No. |  | Type | To terminal unit |  |  | To room | Room label | Pipe type |  | Diameter |  |  | Valve set.
mm
1 |  | Heating/cooling ceiling | 0,1-1-2 |  |  | 0.1 | Living room | PEX pipe |  | 16x2.0 |  |  | 5.5
2 |  | Heating/cooling ceiling | 0,1-2-1 |  |  | 0.1 | Living room | PEX pipe |  | 16x2.0 |  |  | 2.5
3 |  | Heating/cooling ceiling | 0,1-1-1 |  |  | 0.1 | Living room | PEX pipe |  | 16x2.0 |  |  | 5.5
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [11 empty] | - 17 -
Project: Sample project of ceiling heating/cooling system
List of radiant heating components
Product |  |  |  |  | Size |  |  |  | Catalogue code |  | Quantity |  |  | Unit
Basic radiant systems
Manifolds
| Manifold with balancing screws |  |  |  | 3 ways |  |  |  | any producer |  | 1 |  |  | pcs.
Manifold cabinets
| Concealed manifold cabinet |  |  |  | 400x750x160 |  |  |  | any producer |  | 1 |  |  | pcs.
Valves
| Straight ball valve 1'' |  |  |  | 25 |  |  |  | any producer |  | 1 |  |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [11 empty] | - 18 -
Project: Sample project of ceiling heating/cooling system
Manifold board: M4
Storey: |  |  |  | 2
Building unit: |  |  |  | NONE
Type: |  |  |  | Manifold with balancing screws
Number of outlet pairs: |  |  |  | 3
Manifold set: |  |  |  | With ball valve straight
Manifold cabinet: |  |  |  | Concealed manifold cabinet
No. |  | Type | To terminal unit |  |  | To room | Room label | Pipe type |  | Diameter |  |  | Valve set.
mm
1 |  | Heating/cooling ceiling | 0,1-4-1 |  |  | 0.1 | Living room | PEX pipe |  | 16x2.0 |  |  | 8
2 |  | Heating/cooling ceiling | 0,1-3-1 |  |  | 0.1 | Living room | PEX pipe |  | 16x2.0 |  |  | 1.5
3 |  | Heating/cooling ceiling | 0,1-4-2 |  |  | 0.1 | Living room | PEX pipe |  | 16x2.0 |  |  | 7
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [11 empty] | - 19 -
Project: Sample project of ceiling heating/cooling system
List of radiant heating components
Product |  |  |  |  | Size |  |  |  | Catalogue code |  | Quantity |  |  | Unit
Basic radiant systems
Manifolds
| Manifold with balancing screws |  |  |  | 3 ways |  |  |  | any producer |  | 1 |  |  | pcs.
Manifold cabinets
| Concealed manifold cabinet |  |  |  | 400x750x160 |  |  |  | any producer |  | 1 |  |  | pcs.
Valves
| Straight ball valve 1'' |  |  |  | 25 |  |  |  | any producer |  | 1 |  |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [11 empty] | - 20 -

## Radiant system installation
Project: Sample project of ceiling heating/cooling system
Radiant system installation parameters
Heating/cooling zone symbol and thermal resistance of covering | [5 empty] | Occupied / peripheral zone |  | Area |  | Pipe spacing |  |  |  | Pipe type Coil Manner of arrangement Number of circuits |  |  |  | Overall circuit length (feeds + loop) | Valve setting | Heating/cooling surface structure
Symbol<br/>Covering Rλ,B | [5 empty] | Type |  | A |  | VA |  |  |  | Pipe |  |  |  | Ltot | Valve set. | Structure
(m²·K)/W | [7 empty] | m² |  | mm | [7 empty] | m
Double apartment manifold: | [6 empty] | M1, |  | Storey: |  |  | 2, | Bld. unit: |  |  | NONE
No. of outlets: |  |  | 6, | Manifold with balancing screws | [10 empty] | Manifold cabinet type: |  | Concealed manifold cabinet
Supply valve: |  | Lockshield, |  |  | Return valve: | [5 empty] | Thermostatic valve,
Room: 0,8, No. of HZs: 11 / 11, Pipe laying system: Ceiling clip rail system
| 0,8-1-1 None - 0,000 |  |  |  |  | OZ |  | 17.7 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 6 Single pipe meander pattern |  |  |  | 94,2 5,7 + 88,4 | 3 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-1-2 None - 0,000 |  |  |  |  | OZ |  | 17.7 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 5 Single pipe meander pattern |  |  |  | 100,2 11,8 + 88,4 | 3 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-1-3 None - 0,000 |  |  |  |  | OZ |  | 17.7 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 3 Single pipe meander pattern |  |  |  | 106,6 18,1 + 88,4 | 3 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-1-4 None - 0,000 |  |  |  |  | OZ |  | 17.7 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 4 Single pipe meander pattern |  |  |  | 112,6 24,2 + 88,4 | 3 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-1-5 None - 0,000 |  |  |  |  | OZ |  | 17.7 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 2 Single pipe meander pattern |  |  |  | 118,9 30,5 + 88,4 | 3 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-2-1 None - 0,000 |  |  |  |  | OZ |  | 12.6 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 4 Single pipe meander pattern |  |  |  | 77,6 14,7 + 62,9 | 1.5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
Double apartment manifold: | [6 empty] | M2, |  | Storey: |  |  | 2, | Bld. unit: |  |  | NONE
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [20 empty] | - 21 -
Project: Sample project of ceiling heating/cooling system
Symbol<br/>Covering Rλ,B | [5 empty] | Type |  | A |  | VA |  |  |  | Pipe |  |  |  | Ltot | Valve set. | Structure
(m²·K)/W | [7 empty] | m² |  | mm | [7 empty] | m
No. of outlets: |  |  | 5, | Manifold with balancing screws | [10 empty] | Manifold cabinet type: |  | Concealed manifold cabinet
Supply valve: |  | Lockshield, |  |  | Return valve: | [5 empty] | Thermostatic valve,
Room: 0,8, No. of HZs: 11 / 11, Pipe laying system: Ceiling clip rail system
| 0,8-3-1 None - 0,000 |  |  |  |  | OZ |  | 12.5 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 3 Single pipe meander pattern |  |  |  | 75,6 13,2 + 62,4 | 1.5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-4-1 None - 0,000 |  |  |  |  | OZ |  | 22.1 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 3 Single pipe meander pattern |  |  |  | 117,5 7,1 + 110,3 | 5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-4-2 None - 0,000 |  |  |  |  | OZ |  | 22.1 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 2 Single pipe meander pattern |  |  |  | 125,2 14,9 + 110,3 | 5.5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-4-3 None - 0,000 |  |  |  |  | OZ |  | 22.1 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 1 Single pipe meander pattern |  |  |  | 133,1 22,7 + 110,3 | 6.5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,8-4-4 None - 0,000 |  |  |  |  | OZ |  | 22.1 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 1 Single pipe meander pattern |  |  |  | 140,8 30,5 + 110,3 | 8 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
Double apartment manifold: | [6 empty] | M3, |  | Storey: |  |  | 2, | Bld. unit: |  |  | NONE
No. of outlets: |  |  | 3, | Manifold with balancing screws | [10 empty] | Manifold cabinet type: |  | Concealed manifold cabinet
Supply valve: |  | Lockshield, |  |  | Return valve: | [5 empty] | Thermostatic valve,
Room: 0,1, No. of HZs: 6 / 6, Pipe laying system: Ceiling clip rail system
| 0,1-1-1 None - 0,000 |  |  |  |  | OZ |  | 18.3 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 4 Single pipe meander pattern |  |  |  | 100,5 8,7 + 91,7 | 5.5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,1-1-2 None - 0,000 |  |  |  |  | OZ |  | 18.3 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 5 Single pipe meander pattern |  |  |  | 94,5 2,8 + 91,7 | 5.5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,1-2-1 None - 0,000 |  |  |  |  | OZ |  | 12.6 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 8 Single pipe meander pattern |  |  |  | 71,4 8,4 + 63,0 | 2.5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
Double apartment manifold: | [6 empty] | M4, |  | Storey: |  |  | 2, | Bld. unit: |  |  | NONE
No. of outlets: |  |  | 3, | Manifold with balancing screws | [10 empty] | Manifold cabinet type: |  | Concealed manifold cabinet
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [20 empty] | - 22 -
Project: Sample project of ceiling heating/cooling system
Symbol<br/>Covering Rλ,B | [5 empty] | Type |  | A |  | VA |  |  |  | Pipe |  |  |  | Ltot | Valve set. | Structure
(m²·K)/W | [7 empty] | m² |  | mm | [7 empty] | m
Supply valve: |  | Lockshield, |  |  | Return valve: | [5 empty] | Thermostatic valve,
Room: 0,1, No. of HZs: 6 / 6, Pipe laying system: Ceiling clip rail system
| 0,1-3-1 None - 0,000 |  |  |  |  | OZ |  | 6.2 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 2 Single pipe meander pattern |  |  |  | 44,6 13,5 + 31,1 | 1.5 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,1-4-1 None - 0,000 |  |  |  |  | OZ |  | 18.3 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 5 Single pipe meander pattern |  |  |  | 99,7 8,4 + 91,3 | 8 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
| 0,1-4-2 None - 0,000 |  |  |  |  | OZ |  | 18.3 |  | 200 |  |  |  | PEX pipe 16x2.0 Coil 7 Single pipe meander pattern |  |  |  | 94,1 2,8 + 91,3 | 7 | Plaster 0.870 W/(m x K) 2,5 cm (Su 0,6 cm) Rλ,floor = 2,143 (m²·K)/W
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [20 empty] | - 23 -

## Room charts
Project: Sample project of ceiling heating/cooling system
Room chart: 0,1
Storey: | [5 empty] | 1
Building unit: | [5 empty] | 01
Manifolds in room: | [5 empty] | -
Automatic control components: | [5 empty] | -
Heating/cooling ceiling, Structure: 2,243 / 0,025
Heating/cooling zone symbol |  | Occupied / peripheral zone |  | Area |  |  | Pipe spacing |  | Pipe type |  |  | Type of heating-cooling surface | Pipe arrangement | Overall circuit length (feeds + loop) |  | Manifold outlet number
Symbol<br/>Covering Rλ,B |  | Type |  | A |  |  | VA |  | Pipe |  |  | Type | Pipe laying pattern | Ltot |  | Outlet no.
(m²·K)/W |  |  |  | m² |  |  | mm | [6 empty] | m
Double apartment manifold: |  |  | M3, |  | Storey: |  |  | 2, |  | Bld. unit: | NONE
| 0,1-1-1 None - 0,000 | OZ |  | 18.3 |  |  | 200 |  | PEX pipe 16x2.0 Coil 4 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 100,5 8,7 + 91,7 |  | 3
| 0,1-1-2 None - 0,000 | OZ |  | 18.3 |  |  | 200 |  | PEX pipe 16x2.0 Coil 5 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 94,5 2,8 + 91,7 |  | 1
| 0,1-2-1 None - 0,000 | OZ |  | 12.6 |  |  | 200 |  | PEX pipe 16x2.0 Coil 8 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 71,4 8,4 + 63,0 |  | 2
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [14 empty] | - 24 -
Project: Sample project of ceiling heating/cooling system
Heating/cooling zone symbol |  | Occupied / peripheral zone |  | Area |  |  | Pipe spacing |  | Pipe type |  |  | Type of heating-cooling surface | Pipe arrangement | Overall circuit length (feeds + loop) |  | Manifold outlet number
Symbol<br/>Covering Rλ,B |  | Type |  | A |  |  | VA |  | Pipe |  |  | Type | Pipe laying pattern | Ltot |  | Outlet no.
(m²·K)/W |  |  |  | m² |  |  | mm | [6 empty] | m
Double apartment manifold: |  |  | M4, |  | Storey: |  |  | 2, |  | Bld. unit: | NONE
| 0,1-3-1 None - 0,000 | OZ |  | 6.2 |  |  | 200 |  | PEX pipe 16x2.0 Coil 2 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 44,6 13,5 + 31,1 |  | 2
| 0,1-4-1 None - 0,000 | OZ |  | 18.3 |  |  | 200 |  | PEX pipe 16x2.0 Coil 5 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 99,7 8,4 + 91,3 |  | 1
| 0,1-4-2 None - 0,000 | OZ |  | 18.3 |  |  | 200 |  | PEX pipe 16x2.0 Coil 7 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 94,1 2,8 + 91,3 |  | 3
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [14 empty] | - 25 -
Project: Sample project of ceiling heating/cooling system
Room chart: 0,8
Storey: | [5 empty] | 1
Building unit: | [5 empty] | 01
Manifolds in room: | [5 empty] | -
Automatic control components: | [5 empty] | -
Heating/cooling ceiling, Structure: 2,243 / 0,025
Heating/cooling zone symbol |  | Occupied / peripheral zone |  | Area |  |  | Pipe spacing |  | Pipe type |  |  | Type of heating-cooling surface | Pipe arrangement | Overall circuit length (feeds + loop) |  | Manifold outlet number
Symbol<br/>Covering Rλ,B |  | Type |  | A |  |  | VA |  | Pipe |  |  | Type | Pipe laying pattern | Ltot |  | Outlet no.
(m²·K)/W |  |  |  | m² |  |  | mm | [6 empty] | m
Double apartment manifold: |  |  | M1, |  | Storey: |  |  | 2, |  | Bld. unit: | NONE
| 0,8-1-1 None - 0,000 | OZ |  | 17.7 |  |  | 200 |  | PEX pipe 16x2.0 Coil 6 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 94,2 5,7 + 88,4 |  | 6
| 0,8-1-2 None - 0,000 | OZ |  | 17.7 |  |  | 200 |  | PEX pipe 16x2.0 Coil 5 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 100,2 11,8 + 88,4 |  | 5
| 0,8-1-3 None - 0,000 | OZ |  | 17.7 |  |  | 200 |  | PEX pipe 16x2.0 Coil 3 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 106,6 18,1 + 88,4 |  | 4
| 0,8-1-4 None - 0,000 | OZ |  | 17.7 |  |  | 200 |  | PEX pipe 16x2.0 Coil 4 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 112,6 24,2 + 88,4 |  | 3
| 0,8-1-5 None - 0,000 | OZ |  | 17.7 |  |  | 200 |  | PEX pipe 16x2.0 Coil 2 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 118,9 30,5 + 88,4 |  | 2
| 0,8-2-1 None - 0,000 | OZ |  | 12.6 |  |  | 200 |  | PEX pipe 16x2.0 Coil 4 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 77,6 14,7 + 62,9 |  | 1
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [14 empty] | - 26 -
Project: Sample project of ceiling heating/cooling system
Heating/cooling zone symbol |  | Occupied / peripheral zone |  | Area |  |  | Pipe spacing |  | Pipe type |  |  | Type of heating-cooling surface | Pipe arrangement | Overall circuit length (feeds + loop) |  | Manifold outlet number
Symbol<br/>Covering Rλ,B |  | Type |  | A |  |  | VA |  | Pipe |  |  | Type | Pipe laying pattern | Ltot |  | Outlet no.
(m²·K)/W |  |  |  | m² |  |  | mm | [6 empty] | m
Double apartment manifold: |  |  | M2, |  | Storey: |  |  | 2, |  | Bld. unit: | NONE
| 0,8-3-1 None - 0,000 | OZ |  | 12.5 |  |  | 200 |  | PEX pipe 16x2.0 Coil 3 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 75,6 13,2 + 62,4 |  | 1
| 0,8-4-1 None - 0,000 | OZ |  | 22.1 |  |  | 200 |  | PEX pipe 16x2.0 Coil 3 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 117,5 7,1 + 110,3 |  | 5
| 0,8-4-2 None - 0,000 | OZ |  | 22.1 |  |  | 200 |  | PEX pipe 16x2.0 Coil 2 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 125,2 14,9 + 110,3 |  | 4
| 0,8-4-3 None - 0,000 | OZ |  | 22.1 |  |  | 200 |  | PEX pipe 16x2.0 Coil 1 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 133,1 22,7 + 110,3 |  | 3
| 0,8-4-4 None - 0,000 | OZ |  | 22.1 |  |  | 200 |  | PEX pipe 16x2.0 Coil 1 |  |  | Heating/cooling ceiling | Single pipe meander pattern | 140,8 30,5 + 110,3 |  | 2
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 | [14 empty] | - 27 -

## List of pipes, pipe fitting
Project: Sample project of ceiling heating/cooling system
List of pipes, pipe fittings and couplings
Product |  | Size | Catalogue code | Quantity |  | Unit
Copper pipes and fittings EN 1057
Pipes
| Hard copper pipe, Type X bars | 28 x 1,5 |  | 10 |  | m
| Hard copper pipe, Type X bars | 35 x 1,5 |  | 10 |  | m
| Soft copper pipe, Type X coils | 18 x 1 |  | 36 |  | m
| Soft copper pipe, Type X coils | 22 x 1 |  | 45 |  | m
Pipe fittings
| Bend 90° | 18 - 18 |  | 10 |  | pcs.
| Bend 90° | 22 - 22 |  | 12 |  | pcs.
| Coupling | 28 - 18 |  | 2 |  | pcs.
| Coupling FT | 18 - ¾"FT |  | 2 |  | pcs.
| Coupling FT | 22 - ¾"FT |  | 2 |  | pcs.
| Coupling MT | 22 - ½"MT |  | 2 |  | pcs.
| Coupling MT | 22 - ¾"MT |  | 6 |  | pcs.
| Coupling MT | 22 - 1"MT |  | 8 |  | pcs.
| Coupling MT | 28 - ¾"MT |  | 2 |  | pcs.
| Coupling MT | 28 - 1"MT |  | 6 |  | pcs.
| Elbow 90° | 18 - 18 |  | 8 |  | pcs.
| Elbow 90° | 22 - 22 |  | 8 |  | pcs.
| Elbow 90° | 35 - 35 |  | 2 |  | pcs.
| Fitting reducer | 22 - 18 |  | 4 |  | pcs.
| Tee | 28 - 35 - 22 |  | 2 |  | pcs.
| Tee | 22 - 18 - 18 |  | 2 |  | pcs.
| Tee | 22 - 28 - 22 |  | 2 |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 28 -
Project: Sample project of ceiling heating/cooling system
List of insulation
Product |  | Size | Catalogue code | Quantity |  | Unit
Standard insulation catalogue
Lagging
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=18 mm, Th=25 mm |  | 36 |  | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=22 mm, Th=25 mm |  | 45 |  | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=28 mm, Th=40 mm |  | 10 |  | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=35 mm, Th=40 mm |  | 10 |  | m
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 29 -
Project: Sample project of ceiling heating/cooling system
List of valves and fittings
Product |  | Size | Catalogue code | Quantity |  | Unit
Miscellaneous fittings of any make
Other
| Water meter heat counter | ¾"MT, Qnom: 0,6 m³/h | Water meter heat counter | 1 |  | pcs.
| Water meter heat counter | ¾"MT, Qnom: 1 m³/h | Water meter heat counter | 1 |  | pcs.
Neutral valves cataloge - typical construction
Valves
| Ball valve. FT | 20, kvs=40.0 | DN20 | 3 |  | pcs.
| Ball valve. FT | 25, kvs=60.0 | DN25 | 3 |  | pcs.
| Regulatory automatic balancing valve, FT | 15 | DN15 | 1 |  | pcs.
| Regulatory automatic balancing valve, FT | 20 | DN20 | 1 |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 30 -
Project: Sample project of ceiling heating/cooling system
List of radiant heating components
Product |  | Size | Catalogue code | Quantity |  | Unit
Basic radiant systems
Coils
| PEX pipe | 16x2.0, Coil 100 m | any producer | 300 |  | m
| PEX pipe | 16x2.0, Coil 300 m | any producer | 1500 |  | m
Pipe fittings
| Pipe-Manifold fitting 16x3/4 |  | any producer | 34 |  | pcs.
Manifolds
| Manifold with balancing screws | 3 ways | any producer | 2 |  | pcs.
| Manifold with balancing screws | 5 ways | any producer | 1 |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 31 -
Project: Sample project of ceiling heating/cooling system
Product |  | Size | Catalogue code | Quantity |  | Unit
| Manifold with balancing screws | 6 ways | any producer | 1 |  | pcs.
Manifold cabinets
| Concealed manifold cabinet | 400x750x160 | any producer | 3 |  | pcs.
| Concealed manifold cabinet | 500x750x160 | any producer | 1 |  | pcs.
Valves
| Straight ball valve 1'' | 25 | any producer | 4 |  | pcs.
Accessories
| Pipe fastening element 2pcs./m |  | any producer | 3415 |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 32 -
Project: Sample project of ceiling heating/cooling system
Pipes summary
Product |  | Size | Catalogue code | Quantity |  | Unit
Basic radiant systems
Manifolds
| Manifold with balancing screws | 6 ways | any producer | 1 |  | pcs.
Manifold cabinets
| Concealed manifold cabinet | 500x750x160 | any producer | 1 |  | pcs.
Valves
| Straight ball valve 1'' | 25 | any producer | 1 |  | pcs.
Product |  | Size | Catalogue code | Quantity |  | Unit
Standard insulation catalogue
Lagging
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=18 mm, Th=25 mm |  | 36 |  | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=22 mm, Th=25 mm |  | 45 |  | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=28 mm, Th=40 mm |  | 10 |  | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=35 mm, Th=40 mm |  | 10 |  | m
Product |  | Size | Catalogue code | Quantity |  | Unit
Basic radiant systems
Coils
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 33 -
Project: Sample project of ceiling heating/cooling system
Product |  | Size | Catalogue code | Quantity |  | Unit
| PEX pipe | 16x2.0, Coil 100 m | any producer | 300 |  | m
| PEX pipe | 16x2.0, Coil 300 m | any producer | 1500 |  | m
Pipe fittings
| Pipe-Manifold fitting 16x3/4 |  | any producer | 34 |  | pcs.
Manifolds
| Manifold with balancing screws | 3 ways | any producer | 2 |  | pcs.
| Manifold with balancing screws | 5 ways | any producer | 1 |  | pcs.
| Manifold with balancing screws | 6 ways | any producer | 1 |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 34 -
Project: Sample project of ceiling heating/cooling system
Product |  | Size | Catalogue code | Quantity |  | Unit
Manifold cabinets
| Concealed manifold cabinet | 400x750x160 | any producer | 3 |  | pcs.
| Concealed manifold cabinet | 500x750x160 | any producer | 1 |  | pcs.
Valves
| Straight ball valve 1'' | 25 | any producer | 4 |  | pcs.
Accessories
| Pipe fastening element 2pcs./m |  | any producer | 3415 |  | pcs.
Product |  | Size | Catalogue code | Quantity |  | Unit
Basic radiant systems
Manifolds
| Manifold with balancing screws | 3 ways | any producer | 1 |  | pcs.
Manifold cabinets
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 35 -
Project: Sample project of ceiling heating/cooling system
Product |  | Size | Catalogue code | Quantity |  | Unit
| Concealed manifold cabinet | 400x750x160 | any producer | 1 |  | pcs.
Valves
| Straight ball valve 1'' | 25 | any producer | 1 |  | pcs.
Product |  | Size | Catalogue code | Quantity |  | Unit
(Planned components)
Copper pipes and fittings EN 1057
Pipes
| Hard copper pipe, Type X bars | 28 x 1,5 |  | 9.77 |  | m
| Hard copper pipe, Type X bars | 35 x 1,5 |  | 9.85 |  | m
| Soft copper pipe, Type X coils | 18 x 1 |  | 35.22 |  | m
| Soft copper pipe, Type X coils | 22 x 1 |  | 44.54 |  | m
(Insulated)
Copper pipes and fittings EN 1057
Pipes
| Hard copper pipe, Type X bars | 28 x 1,5 |  | 9.77 |  | m
| Hard copper pipe, Type X bars | 35 x 1,5 |  | 9.85 |  | m
| Soft copper pipe, Type X coils | 18 x 1 |  | 35.22 |  | m
| Soft copper pipe, Type X coils | 22 x 1 |  | 44.54 |  | m
(Sized)
Copper pipes and fittings EN 1057
Pipes
| Hard copper pipe, Type X bars | 28 x 1,5 |  | 9.77 |  | m
| Hard copper pipe, Type X bars | 35 x 1,5 |  | 9.85 |  | m
| Soft copper pipe, Type X coils | 18 x 1 |  | 35.22 |  | m
| Soft copper pipe, Type X coils | 22 x 1 |  | 44.54 |  | m
(From radiant systems)
Basic radiant systems
Pipes
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 36 -
Project: Sample project of ceiling heating/cooling system
Product |  | Size | Catalogue code | Quantity |  | Unit
| PEX pipe | 16x2.0 | any producer | 1707.03 |  | m
Product |  | Size | Catalogue code | Quantity |  | Unit
Miscellaneous fittings of any make
Other
| Water meter heat counter | ¾"MT, Qnom: 0,6 m³/h | Water meter heat counter | 1 |  | pcs.
| Water meter heat counter | ¾"MT, Qnom: 1 m³/h | Water meter heat counter | 1 |  | pcs.
Neutral valves cataloge - typical construction
Valves
| Ball valve. FT | 20, kvs=40.0 | DN20 | 3 |  | pcs.
| Ball valve. FT | 25, kvs=60.0 | DN25 | 3 |  | pcs.
| Regulatory automatic balancing valve, FT | 15 | DN15 | 1 |  | pcs.
| Regulatory automatic balancing valve, FT | 20 | DN20 | 1 |  | pcs.
Product |  | Size | Catalogue code | Quantity |  | Unit
Copper pipes and fittings EN 1057
Pipes
| Hard copper pipe, Type X bars | 28 x 1,5 |  | 10 |  | m
| Hard copper pipe, Type X bars | 35 x 1,5 |  | 10 |  | m
| Soft copper pipe, Type X coils | 18 x 1 |  | 36 |  | m
| Soft copper pipe, Type X coils | 22 x 1 |  | 45 |  | m
Pipe fittings
| Bend 90° | 18 - 18 |  | 10 |  | pcs.
| Bend 90° | 22 - 22 |  | 12 |  | pcs.
| Coupling | 28 - 18 |  | 2 |  | pcs.
| Coupling FT | 18 - ¾"FT |  | 2 |  | pcs.
| Coupling FT | 22 - ¾"FT |  | 2 |  | pcs.
| Coupling MT | 22 - ½"MT |  | 2 |  | pcs.
| Coupling MT | 22 - ¾"MT |  | 6 |  | pcs.
| Coupling MT | 22 - 1"MT |  | 8 |  | pcs.
| Coupling MT | 28 - ¾"MT |  | 2 |  | pcs.
| Coupling MT | 28 - 1"MT |  | 6 |  | pcs.
| Elbow 90° | 18 - 18 |  | 8 |  | pcs.
| Elbow 90° | 22 - 22 |  | 8 |  | pcs.
| Elbow 90° | 35 - 35 |  | 2 |  | pcs.
| Fitting reducer | 22 - 18 |  | 4 |  | pcs.
| Tee | 28 - 35 - 22 |  | 2 |  | pcs.
| Tee | 22 - 18 - 18 |  | 2 |  | pcs.
| Tee | 22 - 28 - 22 |  | 2 |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 37 -
Project: Sample project of ceiling heating/cooling system
Product |  | Size | Catalogue code | Quantity |  | Unit
Basic radiant systems
Manifolds
| Manifold with balancing screws | 5 ways | any producer | 1 |  | pcs.
Manifold cabinets
| Concealed manifold cabinet | 400x750x160 | any producer | 1 |  | pcs.
Valves
| Straight ball valve 1'' | 25 | any producer | 1 |  | pcs.
Product |  | Size | Catalogue code | Quantity |  | Unit
Basic radiant systems
Manifolds
| Manifold with balancing screws | 3 ways | any producer | 1 |  | pcs.
Manifold cabinets
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 38 -
Project: Sample project of ceiling heating/cooling system
Product |  | Size | Catalogue code | Quantity |  | Unit
| Concealed manifold cabinet | 400x750x160 | any producer | 1 |  | pcs.
Valves
| Straight ball valve 1'' | 25 | any producer | 1 |  | pcs.
InstalSystem 5 BETA-EN 5.0 (Rev. 15.9.2) © 1996-2015 |  |  |  |  | - 39 -