## Front page
Project
Project number: | 1 | Project version:
Description: | Thermal calculations of buildings
Street: | Moniszki 8b
Postal code and city: | Chorzów | Telephone:
Country: | Poland | Fax:
WWW: | www@instalsoft.com
E-mail: | info@instalsoft.com
Comment
File info
File name: | D:\D-Dokumenty\06-HS\SUZ-HL-v5\ISPROJ\Wynikowy\InstalSoft-InstalSystem5-Heat-loss.isproj
Program version: | 5.0 (Rev. 2.0.A22)
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 |  |  | - 1 -

## General data (building data
Project: Thermal calculations of buildings
General data (building data)
Project name: |  |  |  |  | Thermal calculations of buildings
General data (building data) |  |  |  |  | Date: 30.05.2017
Building parameters
Building structure | [6 empty] | Building sheltering class
[ ] | Detached | [5 empty] | [ ] | Good sheltering
[X] | Multi-apartment | [5 empty] | [ ] | Moderate sheltering
[ ] | Non-residential | [5 empty] | [X] | No sheltering
[ ] | Mixed
Building tightness
Building mass
[7 empty] | [ ] | High
[ ] | Light
[7 empty] | [X] | Medium
[ ] | Medium
[7 empty] | [ ] | Low
[X] | Heavy
Temperatures
External temperature, design |  | θ'e | -20 | °C |  | Internal temperature acc. to standard | [9 empty] | [ ]
Annual mean external temperature |  | θm,e | 7,6 | °C
Dimensions |  |  |  | m
Building width |  | wbld | 12,63 |  |  | Number of storeys |  |  |  |  | N |  |  | 4 |  | [−]
Building length |  | lbld | 12,89 | m |  | Building height |  |  |  |  | hbld |  |  | 8,60 |  | m
Surface area of floor on ground |  | Abld | 162,81 | m2
Ground data
Average building depression* |  | z | 2,00 | m |  | Ground water depth |  |  |  | T |  |  | 10,00 |  |  | m
Perimeter of floor on ground* |  | P | 51,04 | m |  | Corr. factor for temp. fluctuations |  |  |  | fg1 |  |  | 1,45 |  |  | [−]
Char. dim. floor* |  | B' | 6,38 | m |  | Ground water inflow coef. |  |  |  | GW |  |  | 1,00 |  |  | [−]
*may differ from room values
Ventilation
Air change rate at 50 Pa press. diff. | [8 empty] | n50 |  |  | 4,0 |  |  | 1/h
Heat recuperation system efficiency | [8 empty] | ηv |  |  | 0 |  |  | %
Extra heat capacity
[ ] | from building from rooms
[ ]
Temperature drop(in drop phase) | [8 empty] | ΔθRH |  |  | ??? |  |  | K
Init. heating time | [8 empty] | tRH |  |  | 2,0 |  |  | h
Reheat factor | [8 empty] | fRH |  |  | 0,0 |  |  | W/m2
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [11 empty] | - 2 -

## Results for building
Project: Thermal calculations of buildings
Results for building
Project name: | Thermal calculations of buildings
Result list for building | Date: 30.05.2017
Heat loss coefficients | [8 empty] | W/K
Coefficient of heat loss due to heat transfer | ΣHT,e |  |  | 235
Heat loss coefficient due to ventilation | ΣHV |  |  | 124
Total heat loss coefficient | HBld |  |  | 359
Heat loss in building | [8 empty] | W
Total heat loss due to heat transfer | ΦT,Bld |  |  | 9078
Total heat loss due to ventilation
Min. vent. air flux | ΦV,min,Bld = 0,5·ΣΦV,min |  |  | 0
by infiltration | ΦV,inf,Bld = ζ·ΣΦV,inf |  |  | 1788
by mechanical supply ventilation | ΦV,su,Bld |  |  | 0
by exhaust ventilation | ΦV,mech,inf,Bld |  |  | 3006
Total heat loss due to ventilation | ΦV,Bld |  |  | 4793
Standard heat load of building | ΦHL,Bld |  |  | 13871 |  |  |  |  | W
Additional heat load (due to temporary temp. drop) | ΦRH,Bld |  |  | 0 |  |  |  |  | W
Design heat load of building | ΦHL,Des,Bld |  |  | 13871 |  |  |  |  | W
Relative values
Heat load / building heated surf. | AN,Bld | 510 | m² |  | ΦHL,Bld / AN,Bld |  | 27,2 | W/m²
Heat load / building heated cub. | VN,Bld | 1123 | m³ |  | ΦHL,Bld / VN,Bld |  | 12,3 | W/m³
Heat dissipating surface | A | 1978 | m²
Specif. coef. of heat loss due to transm. | HT'
[7 empty] | 0,13 | W/(m²·K)
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [5 empty] | - 3 -

## List of heat losses in room
Project: Thermal calculations of buildings
List of heat losses in rooms
Project name: | [10 empty] | Thermal calculations of buildings
List of heat losses in rooms | [10 empty] | Date: 30.05.2017
Number/Label | [7 empty] | ΦT,e | ΦT | ΦV,min |  | ΦV,inf | ΦV,su | ΦV,m,inf | ΦHL |  | ΦRH | ΦHL,Des
[8 empty] | W | W | W |  | W | W | W | W |  | W | W
Bld. unit |  |  | 01
007 | [7 empty] | 419 | 522 | 0 |  | 222 | 0 | 0 | 744 |  |  | 744
16,0 | °C | 34,34 |  | m² | 75,56 |  | m³
006 | [7 empty] | 224 | 264 | 0 |  | 0 | 0 | 0 | 264 |  |  | 264
16,0 | °C | 11,96 |  | m² | 26,31 |  | m³
002 | [7 empty] | 271 | 338 | 0 |  | 0 | 0 | 0 | 338 |  |  | 338
16,0 | °C | 24,01 |  | m² | 52,82 |  | m³
005 | [7 empty] | 372 | 456 | 0 |  | 174 | 0 | 0 | 631 |  |  | 631
16,0 | °C | 26,98 |  | m² | 59,36 |  | m³
004 | [7 empty] | 414 | 522 | 0 |  | 0 | 0 | 0 | 522 |  |  | 522
16,0 | °C | 35,97 |  | m² | 79,14 |  | m³
Storey |  |  | 0 |  |  |  |  | 1700 |  | 0 |  | 396 | 0 | 0 |  |  | 0
|  | 133,3 |  | m² | 293,2 |  | m³
Number/Label | [7 empty] | ΦT,e | ΦT | ΦV,min |  | ΦV,inf | ΦV,su | ΦV,m,inf | ΦHL |  | ΦRH | ΦHL,Des
[8 empty] | W | W | W |  | W | W | W | W |  | W | W
Bld. unit |  |  | 01
101 / Anteroom | [7 empty] | 0 | 0 | 0 |  | 10 | 0 | 43 | 0 |  |  | 0
-11,5 | °C | 5,60 |  | m² | 13,99 |  | m³
103 / WC | [7 empty] | 416 | 658 | 0 |  | 110 | 0 | 136 | 904 |  |  | 904
20,0 | °C | 13,50 |  | m² | 33,75 |  | m³
104 / Kitchen | [7 empty] | 317 | 656 | 0 |  | 179 | 0 | 328 | 1163 |  |  | 1163
20,0 | °C | 21,96 |  | m² | 54,90 |  | m³
105 / Living room | [7 empty] | 655 | 1016 | 0 |  | 369 | 0 | 408 | 1793 |  |  | 1793
20,0 | °C | 27,12 |  | m² | 67,81 |  | m³
106 / Bathroom | [7 empty] | 431 | 789 | 0 |  | 108 | 0 | 150 | 1046 |  |  | 1046
24,0 | °C | 12,00 |  | m² | 30,00 |  | m³
107 / Living room | [7 empty] | 716 | 1146 | 0 |  | 469 | 0 | 431 | 2046 |  |  | 2046
20,0 | °C | 34,52 |  | m² | 86,30 |  | m³
Bld. unit |  |  | 02 |  |  | Multistorey building unit
102 / Anteroom (Multistorey) | [7 empty] | 363 | 1881 | 0 |  | 0 | 0 | 0 | 1881 |  |  | 1881
20,0 | °C | 24,00 |  | m² | 140,40 |  | m³
Storey |  |  | 1 |  |  |  |  | 2717 |  | 0 |  | 1235 | 0 | 1453 |  |  | 0
|  | 133,1 |  | m² | 343,0 |  | m³
Number/Label | [7 empty] | ΦT,e | ΦT | ΦV,min |  | ΦV,inf | ΦV,su | ΦV,m,inf | ΦHL |  | ΦRH | ΦHL,Des
[8 empty] | W | W | W |  | W | W | W | W |  | W | W
Bld. unit |  |  | 01
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [15 empty] | - 4 -
Project: Thermal calculations of buildings
Number/Label | [7 empty] | ΦT,e | ΦT | ΦV,min |  | ΦV,inf | ΦV,su | ΦV,m,inf | ΦHL |  | ΦRH | ΦHL,Des
[8 empty] | W | W | W |  | W | W | W | W |  | W | W
205 / Bedroom | [7 empty] | 632 | 1009 | 0 |  | 378 | 0 | 486 | 1873 |  |  | 1873
20,0 | °C | 27,81 |  | m² | 69,53 |  | m³
204 / Bedroom | [7 empty] | 310 | 655 | 0 |  | 163 | 0 | 227 | 1044 |  |  | 1044
20,0 | °C | 19,94 |  | m² | 49,84 |  | m³
203 / Bedroom | [7 empty] | 675 | 1044 | 0 |  | 373 | 0 | 486 | 1903 |  |  | 1903
20,0 | °C | 27,41 |  | m² | 68,53 |  | m³
202 / WC | [7 empty] | 426 | 695 | 0 |  | 110 | 0 | 163 | 968 |  |  | 968
20,0 | °C | 13,49 |  | m² | 33,73 |  | m³
206 / Bathroom | [7 empty] | 489 | 900 | 0 |  | 130 | 0 | 269 | 1299 |  |  | 1299
24,0 | °C | 14,45 |  | m² | 36,13 |  | m³
Bld. unit |  |  | 02 |  |  | Multistorey building unit
102 / Anteroom (Multistorey) | [7 empty] | 363 | 1881 | 0 |  | 0 | 0 | 0 | 1881 |  |  | 1881
20,0 | °C | 24,00 |  | m² | 140,40 |  | m³
Storey |  |  | 2 |  |  |  |  | 2714 |  | 0 |  | 1154 | 0 | 1632 |  |  | 0
|  | 127,1 |  | m² | 328,0 |  | m³
Number/Label | [7 empty] | ΦT,e | ΦT | ΦV,min |  | ΦV,inf | ΦV,su | ΦV,m,inf | ΦHL |  | ΦRH | ΦHL,Des
[8 empty] | W | W | W |  | W | W | W | W |  | W | W
Bld. unit |  |  | 01
301 | [7 empty] | 1947 | 2367 | 0 |  | 780 | 0 | 0 | 3147 |  |  | 3147
16,0 | °C | 141,00 |  | m² | 159,35 |  | m³
Storey |  |  | 3 |  |  |  |  | 1947 |  | 0 |  | 780 | 0 | 0 |  |  | 0
|  | 141,0 |  | m² | 159,3 |  | m³
Total for building | [7 empty] | 9078 |  | 0 |  | 3575 | 0 | 3006 |  |  | 0
|  | 510 |  | m² | 1123 |  | m³
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [15 empty] | - 5 -

## Room parameters
Project: Thermal calculations of buildings
Room parameters
Project name: |  |  | Thermal calculations of buildings
Room parameters |  |  | Date: 30.05.2017
Stor./Bld. unit | Number/Label | Room temperature |  | Min. vent. air change rate | fill in when interrupted heating is accounted for
[5 empty] | Temperature decrease duration |  | Init. heating time
|  | θi |  | nmin | tAbs |  | tRH
|  | °C |  | 1/h | h |  | h
0/01 | 007 | 16,0 |  | 0,5
0/01 | 006 | 16,0 |  | 0,5
0/01 | 002 | 16,0 |  | 0,5
0/01 | 005 | 16,0 |  | 0,5
0/01 | 004 | 16,0 |  | 0,5
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [5 empty] | - 6 -
Project: Thermal calculations of buildings
Stor./Bld. unit | Number/Label | Room temperature |  | Min. vent. air change rate | fill in when interrupted heating is accounted for
[5 empty] | Temperature decrease duration |  | Init. heating time
|  | θi |  | nmin | tAbs |  | tRH
|  | °C |  | 1/h | h |  | h
1/01 | 101 / Anteroom | -11,5 (not heated) |  | 0,5
1/01 | 103 / WC | 20,0 |  | 1,5
1/01 | 104 / Kitchen | 20,0 |  | 1,5
1/01 | 105 / Living room | 20,0 |  | 0,5
1/01 | 106 / Bathroom | 24,0 |  | 1,5
1/01 | 107 / Living room | 20,0 |  | 0,5
1/02 | 102 / Anteroom | 20,0 |  | 0,5
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [5 empty] | - 7 -
Project: Thermal calculations of buildings
Stor./Bld. unit | Number/Label | Room temperature |  | Min. vent. air change rate | fill in when interrupted heating is accounted for
[5 empty] | Temperature decrease duration |  | Init. heating time
|  | θi |  | nmin | tAbs |  | tRH
|  | °C |  | 1/h | h |  | h
2/01 | 205 / Bedroom | 20,0 |  | 0,5
2/01 | 204 / Bedroom | 20,0 |  | 0,5
2/01 | 203 / Bedroom | 20,0 |  | 0,5
2/01 | 202 / WC | 20,0 |  | 1,5
2/01 | 206 / Bathroom | 24,0 |  | 1,5
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [5 empty] | - 8 -
Project: Thermal calculations of buildings
Stor./Bld. unit | Number/Label | Room temperature |  | Min. vent. air change rate | fill in when interrupted heating is accounted for
[5 empty] | Temperature decrease duration |  | Init. heating time
|  | θi |  | nmin | tAbs |  | tRH
|  | °C |  | 1/h | h |  | h
3/01 | 301 | 16,0 |  | 0,2
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [5 empty] | - 9 -

## Room data and results
Project: Thermal calculations of buildings
Room data and results
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 0 | [7 empty] | Number/Label |  |  |  |  | 007
Room temperature | [8 empty] | θi,H | 16,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | -0,25 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 34,34 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,50 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,20 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 75,56 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 1,50 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  |  |  | °C
| Perimeter of considered floor slab | [7 empty] | P | 13,69 |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  |  |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | 6,08 |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  |  |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | WG | 1 |  | 4.56 | 1.5 |  | 6.84 |  | 0 |  | 6.84 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 0.8 |  | 29
N |  | EW | 1 |  | 4.56 | 1 |  | 4.56 |  | 0 |  | 4.56 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 1.9 |  | 68
--- |  | IW | 1 |  | 3.99 | 2.5 |  | 9.97 |  | 0 |  | 9.97 |  | j |  |  |  | 16 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 3.48 | 2.5 |  | 8.7 |  | 0 |  | 8.7 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 4.88 | 2.5 |  | 12.21 |  | 1.8 |  | 10.41 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | WG | 1 |  | 9.12 | 1.5 |  | 13.69 |  | 0 |  | 13.69 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 1.59 |  | 57
N |  | EW | 1 |  | 9.12 | 1 |  | 9.12 |  | 0.36 |  | 8.76 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.65 |  | 131
N |  | EWi | 1 |  | 0.6 | 0.6 |  | 0.36 |  | 0 |  | 0.36 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 0.34 |  | 12
--- |  | FL | 1 |  | --- | --- |  | 41.62 |  | 0 |  | 41.62 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.24 |  |  | 3.35 |  | 121
--- |  | IF | 1 |  | --- | --- |  | 41.62 |  | 0 |  | 41.62 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.59 |  |  | 0 | 0.59 |  |  | 2.87 |  | 152
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 14,5 |  | 522
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 18,13 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 0,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 18,13 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 6,2
Standard heat load | [9 empty] | ΦHL | [6 empty] | 21,65 W/m2 | [5 empty] | 9,84 W/m3 | [7 empty] | 744
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 744
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 10 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 0 | [7 empty] | Number/Label |  |  |  |  | 006
Room temperature | [8 empty] | θi,H | 16,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,00 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | -0,25 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 11,96 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,50 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,20 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 26,31 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 1,50 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  |  |  | °C
| Perimeter of considered floor slab | [7 empty] | P | 8,07 |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  |  |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | 3,97 |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  |  |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | WG | 1 |  | 4.56 | 1.5 |  | 6.84 |  | 0 |  | 6.84 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 0.8 |  | 29
N |  | EW | 1 |  | 4.56 | 1 |  | 4.56 |  | 0 |  | 4.56 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 1.9 |  | 68
--- |  | IW | 1 |  | 3.99 | 2.5 |  | 9.97 |  | 0 |  | 9.97 |  | j |  |  |  | 16 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 3 | 2.5 |  | 7.5 |  | 1.8 |  | 5.7 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | WG | 1 |  | 3.51 | 1.5 |  | 5.26 |  | 0 |  | 5.26 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 0.61 |  | 22
N |  | EW | 1 |  | 3.51 | 1 |  | 3.51 |  | 0 |  | 3.51 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 1.46 |  | 53
--- |  | FL | 1 |  | --- | --- |  | 16.01 |  | 0 |  | 16.01 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.27 |  |  | 1.45 |  | 52
--- |  | IF | 1 |  | --- | --- |  | 15.99 |  | 0 |  | 15.99 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.59 |  |  | 0 | 0.59 |  |  | 1.1 |  | 77
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 7,3 |  | 264
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 0,00 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 0,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 0,00 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 0,0
Standard heat load | [9 empty] | ΦHL | [6 empty] | 22,04 W/m2 | [5 empty] | 10,02 W/m3 | [7 empty] | 264
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 264
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 11 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 0 | [7 empty] | Number/Label |  |  |  |  | 002
Room temperature | [8 empty] | θi,H | 16,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,00 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | -0,25 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 24,01 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,50 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,20 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 52,82 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 1,50 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  |  |  | °C
| Perimeter of considered floor slab | [7 empty] | P | 3,25 |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  |  |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | 17,16 |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  |  |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 8 | 2.5 |  | 20.01 |  | 1.8 |  | 18.21 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 3 | 2.5 |  | 7.5 |  | 1.8 |  | 5.7 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | WG | 1 |  | 3.25 | 1.5 |  | 4.88 |  | 0 |  | 4.88 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 0.57 |  | 20
N |  | EW | 1 |  | 3.25 | 1 |  | 3.25 |  | 0 |  | 3.25 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 1.35 |  | 49
--- |  | IW | 1 |  | 4.88 | 2.5 |  | 12.21 |  | 1.8 |  | 10.41 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 3 | 2.5 |  | 7.5 |  | 1.8 |  | 5.7 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | FL | 1 |  | --- | --- |  | 27.9 |  | 0 |  | 27.9 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.16 |  |  | 1.55 |  | 56
--- |  | RO | 1 |  | --- | --- |  | 27.14 |  | 0 |  | 27.14 |  | j |  |  |  | -20 |  | 1 |  | 0.1 |  |  | 0.05 | 0.15 |  |  | 4.06 |  | 146
--- |  | IF | 1 |  | --- | --- |  | 27.14 |  | 0 |  | 27.14 |  | ? |  |  |  | 11.8 |  | 0.12 |  | 0.59 |  |  | 0 | 0.59 |  |  | 1.87 |  | 99
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 9,4 |  | 338
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 0,00 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 0,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 0,00 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 0,0
Standard heat load | [9 empty] | ΦHL | [6 empty] | 14,09 W/m2 | [5 empty] | 6,40 W/m3 | [7 empty] | 338
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 338
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 12 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 0 | [7 empty] | Number/Label |  |  |  |  | 005
Room temperature | [8 empty] | θi,H | 16,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | -0,25 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 26,98 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,50 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,20 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 59,36 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 1,50 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  |  |  | °C
| Perimeter of considered floor slab | [7 empty] | P | 12,38 |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  |  |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | 5,45 |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  |  |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | WG | 1 |  | 8.33 | 1.5 |  | 12.49 |  | 0 |  | 12.49 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 1.45 |  | 52
N |  | EW | 1 |  | 8.33 | 1 |  | 8.33 |  | 0.36 |  | 7.97 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.32 |  | 119
N |  | EWi | 1 |  | 0.6 | 0.6 |  | 0.36 |  | 0 |  | 0.36 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 0.34 |  | 12
--- |  | IW | 1 |  | 4.5 | 2.5 |  | 11.24 |  | 0 |  | 11.24 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 3 | 2.5 |  | 7.5 |  | 1.8 |  | 5.7 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | WG | 1 |  | 4.06 | 1.5 |  | 6.09 |  | 0 |  | 6.09 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 0.71 |  | 25
N |  | EW | 1 |  | 4.06 | 1 |  | 4.06 |  | 0 |  | 4.06 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 1.69 |  | 61
--- |  | IW | 1 |  | 3.48 | 2.5 |  | 8.7 |  | 0 |  | 8.7 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | FL | 1 |  | --- | --- |  | 33.77 |  | 0 |  | 33.77 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.25 |  |  | 2.84 |  | 102
--- |  | IF | 1 |  | --- | --- |  | 33.77 |  | 0 |  | 33.77 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.59 |  |  | 0 | 0.59 |  |  | 2.33 |  | 124
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 12,7 |  | 456
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 14,25 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 0,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 14,25 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 4,8
Standard heat load | [9 empty] | ΦHL | [6 empty] | 23,37 W/m2 | [5 empty] | 10,62 W/m3 | [7 empty] | 631
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 631
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 13 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 0 | [7 empty] | Number/Label |  |  |  |  | 004
Room temperature | [8 empty] | θi,H | 16,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,00 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | -0,25 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 35,97 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,50 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,20 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 79,14 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 1,50 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  |  |  | °C
| Perimeter of considered floor slab | [7 empty] | P | 13,65 |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  |  |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | 6,38 |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  |  |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 8 | 2.5 |  | 20.01 |  | 1.8 |  | 18.21 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 4.5 | 2.5 |  | 11.24 |  | 0 |  | 11.24 |  | j |  |  |  | 16 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | WG | 1 |  | 8.58 | 1.5 |  | 12.86 |  | 0 |  | 12.86 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 1.49 |  | 54
N |  | EW | 1 |  | 8.58 | 1 |  | 8.58 |  | 0 |  | 8.58 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.57 |  | 129
--- |  | WG | 1 |  | 5.07 | 1.5 |  | 7.61 |  | 0 |  | 7.61 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.34 |  |  | 0.88 |  | 32
N |  | EW | 1 |  | 5.07 | 1 |  | 5.07 |  | 0 |  | 5.07 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 2.11 |  | 76
--- |  | FL | 1 |  | --- | --- |  | 43.51 |  | 0 |  | 43.51 |  | g |  |  |  | 7.6 |  | 0.23 |  | --- |  |  | 0.05 | 0.23 |  |  | 3.44 |  | 124
--- |  | IF | 1 |  | --- | --- |  | 17.78 |  | 0 |  | 17.78 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.59 |  |  | 0 | 0.59 |  |  | 1.22 |  | 65
--- |  | IF | 1 |  | --- | --- |  | 25.69 |  | 0 |  | 25.69 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.59 |  |  | 0 | 0.59 |  |  | 1.77 |  | 94
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 14,5 |  | 522
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 0,00 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 0,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 0,00 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 0,0
Standard heat load | [9 empty] | ΦHL | [6 empty] | 14,50 W/m2 | [5 empty] | 6,59 W/m3 | [7 empty] | 522
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 522
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 14 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 1 | [7 empty] | Number/Label |  |  |  |  | 101 / Anteroom
Room temperature | [8 empty] | θi,H | -11,5 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 2,40 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 5,60 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 13,99 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 13,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | 51,04 |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | -2,91 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | 0,00 |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 15,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
N |  | EW | 1 |  | 2.45 | 2.5 |  | 6.12 |  | 0 |  | 6.12 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 2.55 |  | 22
N |  | EW | 1 |  | 2.45 | 2.5 |  | 6.12 |  | 1.8 |  | 4.32 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 1.8 |  | 15
N |  | ED | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.8 |  |  | 0.05 | 0.85 |  |  | 1.53 |  | 13
N |  | EW | 1 |  | 3.7 | 2.5 |  | 9.25 |  | 0 |  | 9.25 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.85 |  | 33
--- |  | EF | 1 |  | --- | --- |  | 9.85 |  | 0 |  | 9.85 |  | e |  |  |  | -20 |  | 1 |  | 0.7 |  |  | 0.05 | 0.75 |  |  | 7.38 |  | 63
--- |  | IW | 1 |  | 2.8 | 2.8 |  | 7.83 |  | 1.8 |  | 6.03 |  | ? |  |  |  | 20 |  | -3.69 |  | 0.35 |  |  | 0.05 | 0.4 |  |  | -8.92 |  | 76
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | -3.69 |  | 2.34 |  |  | 0.05 | 2.39 |  |  | -15.92 |  | 136
--- |  | RO | 1 |  | --- | --- |  | 0.78 |  | 0 |  | 0.78 |  | j |  |  |  | -20 |  | 1 |  | 0.1 |  |  | 0.05 | 0.15 |  |  | 0.12 |  | 1
--- |  | RO | 1 |  | --- | --- |  | 9.06 |  | 0 |  | 9.06 |  | j |  |  |  | -20 |  | 1 |  | 0.1 |  |  | 0.05 | 0.15 |  |  | 1.36 |  | 12
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | -6,2 |  | 0
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 3,36 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 15,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 18,36 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 6,2
Standard heat load | [9 empty] | ΦHL | [6 empty] | 0,00 W/m2 | [5 empty] | 0,00 W/m3 | [7 empty] | 0
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 0
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 15 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 1 | [7 empty] | Number/Label |  |  |  |  | 103 / WC
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 1,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 2,40 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 13,50 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 33,75 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 13,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | 0,17 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 10,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
N |  | EW | 1 |  | 4.85 | 2.8 |  | 13.58 |  | 0 |  | 13.58 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 5.66 |  | 226
--- |  | IW | 1 |  | 4.5 | 2.8 |  | 12.6 |  | 0 |  | 12.6 |  | j |  |  |  | 20 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
N |  | EW | 1 |  | 3.51 | 2.8 |  | 9.83 |  | 1.2 |  | 8.63 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.59 |  | 144
N |  | EWi | 1 |  | 0.8 | 1.5 |  | 1.2 |  | 0 |  | 1.2 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.14 |  | 46
--- |  | IF | 1 |  | --- | --- |  | 17.78 |  | 0 |  | 17.78 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.59 |  |  | 0 | 0.59 |  |  | 1.63 |  | 65
--- |  | IF | 1 |  | --- | --- |  | 17.78 |  | 0 |  | 17.78 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.77 |  | 71
--- |  | IW | 1 |  | 3 | 2.8 |  | 8.4 |  | 1.8 |  | 6.6 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2.01 |  | 80
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 16,4 |  | 658
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 8,10 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 10,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 18,10 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 6,2
Standard heat load | [9 empty] | ΦHL | [6 empty] | 66,97 W/m2 | [5 empty] | 26,79 W/m3 | [7 empty] | 904
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 904
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 16 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 1 | [7 empty] | Number/Label |  |  |  |  | 104 / Kitchen
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 1,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 2,40 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 21,96 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 54,90 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  | 70,00 |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 13,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | 0,17 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 15,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 4.5 | 2.8 |  | 12.6 |  | 1.8 |  | 10.8 |  | j |  |  |  | 20 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 4.5 | 2.8 |  | 12.6 |  | 0 |  | 12.6 |  | j |  |  |  | 20 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
N |  | EW | 1 |  | 5.07 | 2.8 |  | 14.18 |  | 1.8 |  | 12.38 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 5.16 |  | 206
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
--- |  | IF | 1 |  | --- | --- |  | 25.69 |  | 0 |  | 25.69 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.59 |  |  | 0 | 0.59 |  |  | 2.35 |  | 94
--- |  | RO | 1 |  | --- | --- |  | 7.01 |  | 0 |  | 7.01 |  | j |  |  |  | -20 |  | 1 |  | 0.1 |  |  | 0.05 | 0.15 |  |  | 1.05 |  | 42
--- |  | IF | 1 |  | --- | --- |  | 18.69 |  | 0 |  | 18.69 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.86 |  | 75
--- |  | IW | 1 |  | 4.88 | 2.8 |  | 13.66 |  | 1.8 |  | 11.86 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 3.61 |  | 144
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 16,4 |  | 656
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 13,18 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 24,14 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 37,32 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 12,7
Standard heat load | [9 empty] | ΦHL | [6 empty] | 52,97 W/m2 | [5 empty] | 21,19 W/m3 | [7 empty] | 1163
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 1163
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 17 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 1 | [7 empty] | Number/Label |  |  |  |  | 105 / Living room
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,05 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 2,40 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 27,12 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 67,81 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 13,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | 0,17 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 30,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 3.5 | 2.8 |  | 9.8 |  | 0 |  | 9.8 |  | j |  |  |  | 20 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 4.5 | 2.8 |  | 12.6 |  | 1.8 |  | 10.8 |  | j |  |  |  | 20 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0 |  | 0
N |  | EW | 1 |  | 8.33 | 2.8 |  | 23.31 |  | 1.8 |  | 21.51 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 8.96 |  | 358
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
N |  | EW | 1 |  | 4.08 | 2.8 |  | 11.41 |  | 1.8 |  | 9.61 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 4 |  | 160
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
--- |  | IF | 1 |  | --- | --- |  | 33.77 |  | 0 |  | 33.77 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.59 |  |  | 0 | 0.59 |  |  | 3.09 |  | 124
--- |  | IF | 1 |  | --- | --- |  | 15.03 |  | 0 |  | 15.03 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.5 |  | 60
--- |  | IF | 1 |  | --- | --- |  | 18.89 |  | 0 |  | 18.89 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.88 |  | 75
--- |  | IW | 1 |  | 3 | 2.8 |  | 8.4 |  | 0 |  | 8.4 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2.55 |  | 102
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 25,4 |  | 1016
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 27,12 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 30,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 57,12 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 19,4
Standard heat load | [9 empty] | ΦHL | [6 empty] | 66,10 W/m2 | [5 empty] | 26,44 W/m3 | [7 empty] | 1793
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 1793
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 18 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 1 | [7 empty] | Number/Label |  |  |  |  | 106 / Bathroom
Room temperature | [8 empty] | θi,H | 24,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 1,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 2,40 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 12,00 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 30,00 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 13,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | 0,24 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 10,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
N |  | EW | 1 |  | 4.35 | 2.8 |  | 12.18 |  | 0 |  | 12.18 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 5.07 |  | 223
--- |  | IW | 1 |  | 4 | 2.8 |  | 11.2 |  | 1.8 |  | 9.4 |  | j |  |  |  | 20 |  | 0.09 |  | 1 |  |  | 0 | 1 |  |  | 0.85 |  | 38
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | 0.09 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.38 |  | 17
N |  | EW | 1 |  | 3.51 | 2.8 |  | 9.83 |  | 1.2 |  | 8.63 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.59 |  | 158
N |  | EWi | 1 |  | 0.8 | 1.5 |  | 1.2 |  | 0 |  | 1.2 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.14 |  | 50
--- |  | IF | 1 |  | --- | --- |  | 15.99 |  | 0 |  | 15.99 |  | j |  |  |  | 15.8 |  | 0.19 |  | 0.59 |  |  | 0 | 0.59 |  |  | 1.76 |  | 77
--- |  | IF | 1 |  | --- | --- |  | 16.03 |  | 0 |  | 16.03 |  | j |  |  |  | 15.8 |  | 0.19 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.92 |  | 85
--- |  | IW | 1 |  | 3 | 2.8 |  | 8.4 |  | 1.8 |  | 6.6 |  | ? |  |  |  | 15.8 |  | 0.19 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2.41 |  | 106
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.19 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.79 |  | 35
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 17,9 |  | 789
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 7,20 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 10,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 17,20 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 5,8
Standard heat load | [9 empty] | ΦHL | [6 empty] | 87,16 W/m2 | [5 empty] | 34,86 W/m3 | [7 empty] | 1046
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 1046
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 19 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 1 | [7 empty] | Number/Label |  |  |  |  | 107 / Living room
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,05 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 2,40 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 34,52 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 86,30 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  | 40,00 |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 13,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | 0,17 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 30,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 4 | 2.8 |  | 11.2 |  | 1.8 |  | 9.4 |  | j |  |  |  | 24 |  | -0.1 |  | 1 |  |  | 0 | 1 |  |  | -0.94 |  | 38
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | j |  |  |  | --- |  | -0.1 |  | 2.34 |  |  | 0 | 2.34 |  |  | -0.42 |  | 17
N |  | EW | 1 |  | 9.14 | 2.8 |  | 25.59 |  | 3.6 |  | 21.99 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 9.16 |  | 366
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
--- |  | IW | 1 |  | 3.5 | 2.8 |  | 9.8 |  | 0 |  | 9.8 |  | j |  |  |  | 20 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
N |  | EW | 1 |  | 4.57 | 2.8 |  | 12.81 |  | 0 |  | 12.81 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 5.33 |  | 213
--- |  | IF | 1 |  | --- | --- |  | 41.62 |  | 0 |  | 41.62 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.59 |  |  | 0 | 0.59 |  |  | 3.81 |  | 152
--- |  | IF | 1 |  | --- | --- |  | 2.84 |  | 0 |  | 2.84 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.59 |  |  | 0 | 0.59 |  |  | 0.26 |  | 14
--- |  | IF | 1 |  | --- | --- |  | 4.83 |  | 0 |  | 4.83 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 0.48 |  | 19
--- |  | IF | 1 |  | --- | --- |  | 34.15 |  | 0 |  | 34.15 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 3.41 |  | 136
--- |  | IW | 1 |  | 4.88 | 2.8 |  | 13.66 |  | 0 |  | 13.66 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 4.15 |  | 166
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 28,7 |  | 1146
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 34,52 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 31,66 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 66,18 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 22,5
Standard heat load | [9 empty] | ΦHL | [6 empty] | 59,28 W/m2 | [5 empty] | 23,71 W/m3 | [7 empty] | 2046
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 2046
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 20 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 02 |  |  | Storey |  |  |  | 1 | [7 empty] | Number/Label |  |  |  |  | 102 / Anteroom
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,00 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 3,80 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 24,00 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 5,30 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 140,40 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  |  |  | °C
| Perimeter of considered floor slab | [7 empty] | P | 51,04 |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  |  |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | 6,38 |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  |  |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 1.2 | 2.8 |  | 3.35 |  | 0 |  | 3.35 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1 |  |  | 0 | 1 |  |  | 0.52 |  | 21
--- |  | IW | 1 |  | 2.8 | 2.8 |  | 7.83 |  | 1.8 |  | 6.03 |  | ? |  |  |  | -11.5 |  | 0.79 |  | 0.35 |  |  | 0.05 | 0.4 |  |  | 1.9 |  | 76
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.79 |  | 2.34 |  |  | 0.05 | 2.39 |  |  | 3.39 |  | 136
--- |  | IW | 1 |  | 4.88 | 2.8 |  | 13.66 |  | 1.8 |  | 11.86 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 3.61 |  | 144
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
--- |  | IW | 1 |  | 3 | 2.8 |  | 8.4 |  | 1.8 |  | 6.6 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2.01 |  | 80
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
--- |  | IW | 1 |  | 3 | 2.8 |  | 8.4 |  | 1.8 |  | 6.6 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2 |  | 80
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
N |  | EW | 1 |  | 3.25 | 2.8 |  | 9.1 |  | 0 |  | 9.1 |  | j |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.79 |  | 152
--- |  | IW | 1 |  | 3 | 2.8 |  | 8.4 |  | 1.8 |  | 6.6 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2.01 |  | 106
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 35
--- |  | IW | 1 |  | 4.88 | 2.8 |  | 13.66 |  | 0 |  | 13.66 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 4.15 |  | 166
--- |  | IW | 1 |  | 4.45 | 2.8 |  | 12.45 |  | 1.8 |  | 10.65 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 3.24 |  | 130
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
--- |  | IW | 1 |  | 3 | 2.8 |  | 8.4 |  | 0 |  | 8.4 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2.55 |  | 102
--- |  | IW | 1 |  | 4.88 | 2.8 |  | 13.66 |  | 1.8 |  | 11.86 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1 |  |  | 0 | 1 |  |  | 1.84 |  | 74
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
--- |  | IW | 1 |  | 4.25 | 2.8 |  | 11.9 |  | 1.8 |  | 10.1 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 3.07 |  | 123
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
--- |  | IW | 1 |  | 3.61 | 2.8 |  | 10.11 |  | 1.8 |  | 8.31 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2.52 |  | 134
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 35
--- |  | IF | 1 |  | --- | --- |  | 27.14 |  | 0 |  | 27.14 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 0.59 |  |  | 0 | 0.59 |  |  | 2.48 |  | 99
--- |  | IF | 1 |  | --- | --- |  | 27.14 |  | 0 |  | 27.14 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 2.71 |  | 108
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 47,0 |  | 1881
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 21 -
Project: Thermal calculations of buildings
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 0,00 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 0,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 0,00 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 0,0
Standard heat load | [9 empty] | ΦHL | [6 empty] | 78,37 W/m2 | [5 empty] | 13,40 W/m3 | [7 empty] | 1881
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 1881
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 22 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 2 | [7 empty] | Number/Label |  |  |  |  | 205 / Bedroom
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,05 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 5,20 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 27,81 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 69,53 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  | 40,00 |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 22,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | -0,06 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 36,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 4 | 2.8 |  | 11.21 |  | 0 |  | 11.21 |  | j |  |  |  | 24 |  | -0.1 |  | 1 |  |  | 0 | 1 |  |  | -1.12 |  | 45
N |  | EW | 1 |  | 3.39 | 2.8 |  | 9.49 |  | 0 |  | 9.49 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.95 |  | 158
N |  | EW | 1 |  | 8.52 | 2.8 |  | 23.86 |  | 3.6 |  | 20.26 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 8.44 |  | 337
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
--- |  | IW | 1 |  | 1 | 2.8 |  | 2.8 |  | 0 |  | 2.8 |  | j |  |  |  | 20 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 3.5 | 2.8 |  | 9.8 |  | 0 |  | 9.8 |  | j |  |  |  | 20 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
--- |  | IF | 1 |  | --- | --- |  | 34.15 |  | 0 |  | 34.15 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 3.41 |  | 136
--- |  | IF | 1 |  | --- | --- |  | 34.15 |  | 0 |  | 34.15 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 3.41 |  | 136
--- |  | IW | 1 |  | 4.25 | 2.8 |  | 11.9 |  | 1.8 |  | 10.1 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 3.07 |  | 123
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 25,2 |  | 1009
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 27,81 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 35,76 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 63,57 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 21,6
Standard heat load | [9 empty] | ΦHL | [6 empty] | 67,36 W/m2 | [5 empty] | 26,95 W/m3 | [7 empty] | 1873
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 1873
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 23 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 2 | [7 empty] | Number/Label |  |  |  |  | 204 / Bedroom
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 5,20 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 19,94 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 49,84 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  | 40,00 |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 22,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | -0,06 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 18,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
N |  | EW | 1 |  | 5.82 | 2.8 |  | 16.3 |  | 1.8 |  | 14.5 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 6.04 |  | 242
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
--- |  | IW | 1 |  | 1 | 2.8 |  | 2.8 |  | 0 |  | 2.8 |  | j |  |  |  | 20 |  | 0 |  | 1.96 |  |  | 0 | 1.96 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 3.5 | 2.8 |  | 9.8 |  | 0 |  | 9.8 |  | j |  |  |  | 20 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
--- |  | IW | 1 |  | 3.5 | 2.8 |  | 9.8 |  | 0 |  | 9.8 |  | j |  |  |  | 20 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
--- |  | IF | 1 |  | --- | --- |  | 4.83 |  | 0 |  | 4.83 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 0.48 |  | 19
--- |  | IF | 1 |  | --- | --- |  | 18.89 |  | 0 |  | 18.89 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.88 |  | 75
--- |  | IF | 1 |  | --- | --- |  | 23.72 |  | 0 |  | 23.72 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 2.37 |  | 95
--- |  | IW | 1 |  | 4.45 | 2.8 |  | 12.45 |  | 1.8 |  | 10.65 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 3.24 |  | 130
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 16,4 |  | 655
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 11,96 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 16,68 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 28,64 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 9,7
Standard heat load | [9 empty] | ΦHL | [6 empty] | 52,38 W/m2 | [5 empty] | 20,95 W/m3 | [7 empty] | 1044
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 1044
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 24 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 2 | [7 empty] | Number/Label |  |  |  |  | 203 / Bedroom
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,05 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 5,20 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 27,41 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 68,53 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  | 40,00 |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 22,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | -0,06 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 36,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 3.18 | 2.8 |  | 8.9 |  | 0 |  | 8.9 |  | j |  |  |  | 20 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
N |  | EW | 1 |  | 3.69 | 2.8 |  | 10.33 |  | 0 |  | 10.33 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 4.3 |  | 172
N |  | EW | 1 |  | 9.14 | 2.8 |  | 25.59 |  | 3.6 |  | 21.99 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 9.16 |  | 366
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 68
--- |  | IW | 1 |  | 3.5 | 2.8 |  | 9.8 |  | 0 |  | 9.8 |  | j |  |  |  | 20 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
--- |  | IF | 1 |  | --- | --- |  | 15.03 |  | 0 |  | 15.03 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.5 |  | 60
--- |  | IF | 1 |  | --- | --- |  | 18.69 |  | 0 |  | 18.69 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.86 |  | 75
--- |  | IF | 1 |  | --- | --- |  | 33.72 |  | 0 |  | 33.72 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 3.36 |  | 135
--- |  | IW | 1 |  | 4.88 | 2.8 |  | 13.66 |  | 1.8 |  | 11.86 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1 |  |  | 0 | 1 |  |  | 1.84 |  | 74
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 26,1 |  | 1044
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 27,41 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 35,76 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 63,17 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 21,5
Standard heat load | [9 empty] | ΦHL | [6 empty] | 69,42 W/m2 | [5 empty] | 27,77 W/m3 | [7 empty] | 1903
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 1903
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 25 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 2 | [7 empty] | Number/Label |  |  |  |  | 202 / WC
Room temperature | [8 empty] | θi,H | 20,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 1,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 5,20 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 13,49 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 33,73 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 22,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | -0,06 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 12,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 3.18 | 2.8 |  | 8.9 |  | 0 |  | 8.9 |  | j |  |  |  | 20 |  | 0 |  | 1 |  |  | 0 | 1 |  |  | 0 |  | 0
N |  | EW | 1 |  | 5.07 | 2.8 |  | 14.21 |  | 0 |  | 14.21 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 5.92 |  | 237
N |  | EW | 1 |  | 3.51 | 2.8 |  | 9.83 |  | 1.2 |  | 8.63 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.59 |  | 144
N |  | EWi | 1 |  | 0.8 | 1.5 |  | 1.2 |  | 0 |  | 1.2 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.14 |  | 46
--- |  | IF | 1 |  | --- | --- |  | 17.78 |  | 0 |  | 17.78 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.77 |  | 71
--- |  | IF | 1 |  | --- | --- |  | 17.81 |  | 0 |  | 17.81 |  | j |  |  |  | 13.8 |  | 0.16 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.78 |  | 71
--- |  | IW | 1 |  | 1.2 | 2.8 |  | 3.35 |  | 0 |  | 3.35 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1 |  |  | 0 | 1 |  |  | 0.52 |  | 21
--- |  | IW | 1 |  | 3 | 2.8 |  | 8.4 |  | 1.8 |  | 6.6 |  | ? |  |  |  | 13.8 |  | 0.16 |  | 1.96 |  |  | 0 | 1.96 |  |  | 2 |  | 80
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.16 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.65 |  | 26
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 17,4 |  | 695
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 8,09 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 12,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 20,09 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 6,8
Standard heat load | [9 empty] | ΦHL | [6 empty] | 71,78 W/m2 | [5 empty] | 28,71 W/m3 | [7 empty] | 968
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 968
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 26 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 2 | [7 empty] | Number/Label |  |  |  |  | 206 / Bathroom
Room temperature | [8 empty] | θi,H | 24,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 1,5 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,03 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 5,20 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 14,45 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,80 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,30 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 2,50 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 36,13 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  | 22,4 |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  | 0,04 |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  | 18,00 |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
--- |  | IW | 1 |  | 4 | 2.8 |  | 11.21 |  | 0 |  | 11.21 |  | j |  |  |  | 20 |  | 0.09 |  | 1 |  |  | 0 | 1 |  |  | 1.02 |  | 45
N |  | EW | 1 |  | 4.13 | 2.8 |  | 11.56 |  | 1.8 |  | 9.76 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 4.07 |  | 179
N |  | EWi | 1 |  | 1.2 | 1.5 |  | 1.8 |  | 0 |  | 1.8 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 1.71 |  | 75
N |  | EW | 1 |  | 4.58 | 2.8 |  | 12.82 |  | 0 |  | 12.82 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 5.34 |  | 235
--- |  | IF | 1 |  | --- | --- |  | 16.03 |  | 0 |  | 16.03 |  | j |  |  |  | 15.8 |  | 0.19 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.92 |  | 85
--- |  | IF | 1 |  | --- | --- |  | 2.84 |  | 0 |  | 2.84 |  | j |  |  |  | 15.8 |  | 0.19 |  | 0.59 |  |  | 0 | 0.59 |  |  | 0.31 |  | 14
--- |  | IF | 1 |  | --- | --- |  | 18.89 |  | 0 |  | 18.89 |  | j |  |  |  | 15.8 |  | 0.19 |  | 0.64 |  |  | 0 | 0.64 |  |  | 2.27 |  | 100
--- |  | IW | 1 |  | 3.61 | 2.8 |  | 10.11 |  | 1.8 |  | 8.31 |  | ? |  |  |  | 15.8 |  | 0.19 |  | 1.96 |  |  | 0 | 1.96 |  |  | 3.04 |  | 134
--- |  | ID | 1 |  | 0.9 | 2 |  | 1.8 |  | 0 |  | 1.8 |  | ? |  |  |  | --- |  | 0.19 |  | 2.34 |  |  | 0 | 2.34 |  |  | 0.79 |  | 35
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 20,5 |  | 900
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 8,67 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 18,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 26,67 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 9,1
Standard heat load | [9 empty] | ΦHL | [6 empty] | 89,89 W/m2 | [5 empty] | 35,96 W/m3 | [7 empty] | 1299
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 1299
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 27 -
Project: Thermal calculations of buildings
Project name: | [14 empty] | Thermal calculations of buildings
Heat load of room | [14 empty] | Date: 30.05.2017
Bld. unit |  |  |  | 01 |  |  | Storey |  |  |  | 3 | [7 empty] | Number/Label |  |  |  |  | 301
Room temperature | [8 empty] | θi,H | 16,0 |  |  | °C |  | Infiltration
Min. vent. air change rate | [8 empty] | nmin | 0,2 |  |  | 1/h |  |  | Tightness | [10 empty] | n50 |  |  | 4,0 |  | 1/h
Dimensions | [15 empty] | Shelter factor | [10 empty] | e |  |  | 0,05 |  | [−]
| Width of room | [7 empty] | wf | --- |  |  | m |  |  | Elevation above ground | [10 empty] | h |  |  | 7,60 |  | m
| Length of room | [7 empty] | lf | --- |  |  | m |  |  | Elevation correction coefficient | [10 empty] | ε |  |  | 1,0 |  | [−]
| Area of room | [7 empty] | Af | 141,00 |  |  | m² |  | Mechanical ventilation
| Height of storeys within axes | [7 empty] | ha | 2,00 |  |  | m |  |  | Supplied air volume flux | [10 empty] | Vsu |  |  |  |  | m³/h
| Floor thickness | [7 empty] | dflo | 0,40 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θsu |  |  |  |  | °C
| Height of room | [7 empty] | hf | 1,60 |  |  | m |  |  | - Temp. red. coef. | [10 empty] | fV,sup |  |  |  |  | [−]
| Room cubic capacity | [7 empty] | VR | 159,35 |  |  | m³ |  |  | Exhaust air volume flux | [10 empty] | Vex |  |  |  |  | m³/h
Ground | [15 empty] | Mech. infiltration from adjacent rooms | [10 empty] | Vmech,inf,ij |  |  |  |  | m³/h
| Depression below ground level | [7 empty] | z | 0,00 |  |  | m |  |  | Average temp. of air infiltrating from adjacent rooms | [10 empty] | θmech,inf, ij |  |  |  |  | °C
| Perimeter of considered floor slab | [7 empty] | P | ??? |  |  | m |  |  | - Temp. red. factor | [10 empty] | fV,mech,inf |  |  |  |  | [−]
| Char. dim. floor [X] for room | [7 empty] | B' | ??? |  |  | m |  |  | Mech. infiltration from outside | [10 empty] | Vmech,inf,e |  |  |  |  | m³/h
1 |  | 2 | 3 |  | 4 | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  |  |  | 10 |  | 11 |  | 12 |  |  | 13 | 14 |  |  | 15 |  | 16
Partition orientation |  | Partition type | Quantity |  | Width | Length / Height |  | Gross area |  | Wind./door area |  | Net area |  | Heat loss to |  |  |  | Temperature on other side |  | Correction factor |  | Heat transfer coefficient |  |  | Allowance for thermal bridges | Adjusted heat transfer coefficient |  |  | Heat loss coefficient |  | Heat loss across partition
|  |  | n |  | b | l/h |  | AGross |  | ADeduct |  | ANet |  | e/u<br/>g/j |  |  |  | θos |  | ek/bu<br/>fij/fg2 |  | U |  |  | ΔU | Uc/equiv |  |  | HT |  | ΦT
[5 empty] | m |  |  | m² | [9 empty] | °C |  |  |  | W/(m²·K) | [6 empty] | W/K |  | W
N |  | EW | 1 |  | --- | --- |  | 14.13 |  | 0.36 |  | 13.77 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 5.73 |  | 206
N |  | EWi | 1 |  | 0.6 | 0.6 |  | 0.36 |  | 0 |  | 0.36 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 0.34 |  | 12
N |  | EW | 1 |  | 12.65 | 0.63 |  | 7.96 |  | 0 |  | 7.96 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.32 |  | 119
N |  | EW | 1 |  | --- | --- |  | 14.13 |  | 0.36 |  | 13.77 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 5.73 |  | 206
N |  | EWi | 1 |  | 0.6 | 0.6 |  | 0.36 |  | 0 |  | 0.36 |  | e |  |  |  | --- |  | 1 |  | 0.9 |  |  | 0.05 | 0.95 |  |  | 0.34 |  | 12
N |  | EW | 1 |  | 12.65 | 0.63 |  | 7.99 |  | 0 |  | 7.99 |  | e |  |  |  | -20 |  | 1 |  | 0.37 |  |  | 0.05 | 0.42 |  |  | 3.33 |  | 120
--- |  | IF | 1 |  | --- | --- |  | 17.81 |  | 0 |  | 17.81 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.34 |  | 71
--- |  | IF | 1 |  | --- | --- |  | 18.89 |  | 0 |  | 18.89 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.42 |  | 100
--- |  | IF | 1 |  | --- | --- |  | 33.72 |  | 0 |  | 33.72 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.64 |  |  | 0 | 0.64 |  |  | 2.53 |  | 135
--- |  | IF | 1 |  | --- | --- |  | 23.72 |  | 0 |  | 23.72 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.64 |  |  | 0 | 0.64 |  |  | 1.78 |  | 95
--- |  | IF | 1 |  | --- | --- |  | 34.15 |  | 0 |  | 34.15 |  | j |  |  |  | 11.8 |  | 0.12 |  | 0.64 |  |  | 0 | 0.64 |  |  | 2.56 |  | 136
--- |  | IF | 1 |  | --- | --- |  | 27.14 |  | 0 |  | 27.14 |  | ? |  |  |  | 11.8 |  | 0.12 |  | 0.64 |  |  | 0 | 0.64 |  |  | 2.04 |  | 108
--- |  | RO | 1 |  | --- | --- |  | 80.08 |  | 0 |  | 80.08 |  | j |  |  |  | -20 |  | 1 |  | 0.16 |  |  | 0.05 | 0.21 |  |  | 17.11 |  | 616
--- |  | RO | 1 |  | --- | --- |  | 85.06 |  | 0 |  | 85.06 |  | j |  |  |  | -20 |  | 1 |  | 0.16 |  |  | 0.05 | 0.21 |  |  | 18.17 |  | 654
Heat loss due to heat transfer | [9 empty] | HT / ΦT | [18 empty] | 65,7 |  | 2367
| Min. vent. air flux | [8 empty] | Vmin | [12 empty] | m³/h
| by infiltration | [8 empty] | Vinf | [10 empty] | 63,74 |  | m³/h
| by mechanical supply ventilation | [8 empty] | Vsup · fV,sup | [10 empty] | 0,00 |  | m³/h
| by exhaust ventilation | [8 empty] | Vmech,inf,e + Vmech,inf,ij · fv,mech,inf,ij | [10 empty] | 0,00 |  | m³/h
Ventilation air flux | [9 empty] | V | [10 empty] | 63,74 |  | m³/h
Heat loss due to ventilation | [9 empty] | HV / ΦV | [18 empty] | 21,7
Standard heat load | [9 empty] | ΦHL | [6 empty] | 22,32 W/m2 | [5 empty] | 19,75 W/m3 | [7 empty] | 3147
Additional heat load (due to temporary temp. drop) | [9 empty] | ΦRH |  |  |  |  | fRH = 0,0 W/m² | [15 empty] | 0
Design heat load | [9 empty] | ΦHL,Des | [20 empty] | 3147
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [27 empty] | - 28 -

## Data and results for partit
Project: Thermal calculations of buildings
Data and results for partitions
Partition definition name: |  | ExW 0.45
Heat transfer coefficient: |  | 0,37 W/(m²·K)
Description: |  | External wall 0.45
Heat flow direction: |  | Horizontal
Partition type: |  | External wall
Heat capt. res. (int.): |  | 0,130 (m²·K)/W
Heat capt. res. (ext.): |  | 0,040 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Tynk gipsowy |  | 0.01 | 0.35 | 0 | 1000 | 1000 |  | 0.029
2 | Styropian |  | 0.09 | 0.043 | 0 | 1460 | 1000 |  | 2.093
3 | Lekkie cegły |  | 0.35 | 0.8 | 0 | 880 | 1000 |  | 0.438
Condensation occurs inside partition!
Internal temperature: |  | 20 °C
Internal humidity: |  | 60 %
External temperature: |  | -10 °C
External humidity: |  | 90 %
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 30 -
Project: Thermal calculations of buildings
Partition definition name: |  | ExW 0.3
Heat transfer coefficient: |  | 0,41 W/(m²·K)
Description: |  | External wall 0.3
Heat flow direction: |  | Horizontal
Partition type: |  | External wall
Heat capt. res. (int.): |  | 0,100 (m²·K)/W
Heat capt. res. (ext.): |  | 0,100 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Plaster 1200 (EN 12524) |  | 0.01 | 0.43 | 4 | 1000 | 1200 |  | 0.023
2 | mineral and plant fibre insulating materials-DIN 18165 group 040 (8) |  | 0.08 | 0.04 | 1 | 750 | 8 |  | 2
3 | 2 K concrete hollow bricks, width b=240 mm-DIN 18153 |  | 0.2 | 0.92 | 20 | 880 | 1800 |  | 0.217
4 | Lime and sand plaster (EN 12524) |  | 0.01 | 1 | 6 | 1000 | 1800 |  | 0.01
Condensation occurs inside partition!
Internal temperature: |  | 20 °C
Internal humidity: |  | 60 %
External temperature: |  | -10 °C
External humidity: |  | 90 %
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 31 -
Project: Thermal calculations of buildings
Partition definition name: |  | WG 0.45
Description: |  | Wall adjacent to ground 0.45
Heat flow direction: |  | Horizontal
Partition type: |  | Wall near ground
Heat capt. res. (int.): |  | 0,130 (m²·K)/W
Costam
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Tynk, gładź cem.-wap. |  | 0.015 | 0.82 | 13.6 | 840 | 1850 |  | 0.018
2 | Styropian (40) |  | 0.075 | 0.042 | 50.99 | 1460 | 40 |  | 1.786
3 | Mur z cegły cer. |  | 0.35 | 0.77 | 5.83 | 880 | 1800 |  | 0.455
4 | Papa (asfaltowa) |  | 0.01 | 0.18 | 0.94 | 1460 | 1000 |  | 0.056
Partition definition name: |  | InW 0.3
Heat transfer coefficient: |  | 0,83 W/(m²·K)
Description: |  | Internal wall 0.3
Heat flow direction: |  | Horizontal
Partition type: |  | Internal wall
Heat capt. res. (int.): |  | 0,130 (m²·K)/W
Heat capt. res. (ext.): |  | 0,130 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Plaster 900 (EN 12524) |  | 0.01 | 0.3 | 4 | 1000 | 900 |  | 0.033
2 | 3 K hollow brick made of lightweight concrete, width 300 mm-DIN 18151 (600) |  | 0.28 | 0.32 | 5 | 880 | 600 |  | 0.875
3 | Plaster 900 (EN 12524) |  | 0.01 | 0.3 | 4 | 1000 | 900 |  | 0.033
Partition definition name: |  | InW 0.45
Heat transfer coefficient: |  | 0,35 W/(m²·K)
Description: |  | Internal wall 0.45
Heat flow direction: |  | Horizontal
Partition type: |  | Internal wall
Heat capt. res. (int.): |  | 0,130 (m²·K)/W
Heat capt. res. (ext.): |  | 0,130 (m²·K)/W
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 32 -
Project: Thermal calculations of buildings
Partition definition name: |  | InW 0.25
Heat transfer coefficient: |  | 1,96 W/(m²·K)
Description: |  | Internal wall 0.25
Heat flow direction: |  | Horizontal
Partition type: |  | Internal wall
Heat capt. res. (int.): |  | 0,130 (m²·K)/W
Heat capt. res. (ext.): |  | 0,130 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Tynk, gładź cem. |  | 0.01 | 1 | 13.6 | 840 | 2000 |  | 0.01
2 | Mur (silikaty) |  | 0.23 | 1 | 5.83 | 880 | 1900 |  | 0.23
3 | Tynk, gładź cem. |  | 0.01 | 1 | 13.6 | 840 | 2000 |  | 0.01
Partition definition name: |  | Id
Heat transfer coefficient: |  | 2,34 W/(m²·K)
Description: |  | Internal door
Heat flow direction: |  | Horizontal
Partition type: |  | Internal door
Heat capt. res. (int.): |  | 0,130 (m²·K)/W
Heat capt. res. (ext.): |  | 0,130 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Timber 700 (EN 12524) |  | 0.03 | 0.18 | 50 | 1600 | 700 |  | 0.167
Partition definition name: |  | Ed
Heat transfer coefficient: |  | 0,80 W/(m²·K)
Description: |  | External door insulated
Heat flow direction: |  | Horizontal
Partition type: |  | External door
Heat capt. res. (int.): |  | 0,130 (m²·K)/W
Heat capt. res. (ext.): |  | 0,040 (m²·K)/W
Partition definition name: |  | Slab
Heat transfer coefficient: |  | 0,59 W/(m²·K)
Description: |  | Internal slab 0.3
Heat flow direction: |  | Down
Partition type: |  | Internal floor
Heat capt. res. (int.): |  | 0,170 (m²·K)/W
Heat capt. res. (ext.): |  | 0,170 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Beton zwykły (1900) |  | 0.04 | 1 | 8.16 | 840 | 1900 |  | 0.04
2 | Styropian (40) |  | 0.05 | 0.042 | 50.99 | 1460 | 40 |  | 1.19
3 | Żelbet (2500) |  | 0.21 | 1.7 | 20.4 | 840 | 2500 |  | 0.124
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 33 -
Project: Thermal calculations of buildings
Partition definition name: |  | Rf 0.3
Heat transfer coefficient: |  | 0,10 W/(m²·K)
Description: |  | Roof 0.3
Heat flow direction: |  | Up
Partition type: |  | Roof
Heat capt. res. (int.): |  | 0,100 (m²·K)/W
Heat capt. res. (ext.): |  | 0,040 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Tiles (roof) - ceramic (EN 12524) |  | 0.05 | 1 | 30 | 800 | 2000 |  | 0.05
2 | Elastic PVC, with 40% plastifier (EN 12524) |  | 0.01 | 0.14 | 100000 | 1000 | 1200 |  | 0.071
3 | polyurethane (PUR)-hard foamed plastic group 020 |  | 0.19 | 0.02 | 65 | 1460 | 30 |  | 9.5
4 | Timber 700 (EN 12524) |  | 0.05 | 0.18 | 50 | 1600 | 700 |  | 0.278
Internal temperature: |  | 20 °C
Internal humidity: |  | 60 %
External temperature: |  | -10 °C
External humidity: |  | 90 %
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 34 -
Project: Thermal calculations of buildings
Partition definition name: |  | FlG 0.5
Description: |  | Floor on ground 0.5
Heat flow direction: |  | Down
Partition type: |  | Floor on ground
Heat capt. res. (int.): |  | 0,170 (m²·K)/W
Costam
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Beton |  | 0.03 | 1.75 | 0 | 840 | 1000 |  | 0.017
2 | Styropian |  | 0.06 | 0.043 | 0 | 1460 | 1000 |  | 1.395
3 | Beton |  | 0.15 | 1.75 | 0 | 840 | 1000 |  | 0.086
4 | Papa |  | 0.002 | 0.23 | 0 | 1460 | 1000 |  | 0.009
5 | Żwir z EN 12831 |  | 0.258 | 0.7 | 0 | 840 | 1000 |  | 0.369
Partition definition name: |  | Rf 0.4
Heat transfer coefficient: |  | 0,16 W/(m²·K)
Description: |  | Joisted roof 0.4
Heat flow direction: |  | Up
Partition type: |  | Roof
Heat capt. res. (int.): |  | 0,100 (m²·K)/W
Heat capt. res. (ext.): |  | 0,040 (m²·K)/W
Partition definition name: |  | FlG 0.3
Description: |  | Floor on ground 0.3
Heat flow direction: |  | Down
Partition type: |  | Floor on ground
Heat capt. res. (int.): |  | 0,170 (m²·K)/W
Costam
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Beton (1400) |  | 0.05 | 0.72 | 4.08 | 840 | 1400 |  | 0.069
2 | Styropian (40) |  | 0.05 | 0.042 | 50.99 | 1460 | 40 |  | 1.19
3 | Beton zwykły (2200) |  | 0.2 | 1.3 | 13.6 | 840 | 2200 |  | 0.154
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 35 -
Project: Thermal calculations of buildings
Partition definition name: |  | Dach a
Heat transfer coefficient: |  | 0,14 W/(m²·K)
Description: |  | Part of composite roof
Heat flow direction: |  | Up
Partition type: |  | Roof
Heat capt. res. (int.): |  | 0,100 (m²·K)/W
Heat capt. res. (ext.): |  | 0,040 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Płyty |  | 0.02 | 0.23 | 8.16 | 1000 | 1000 |  | 0.087
2 | Wełna min. (40) |  | 0.34 | 0.05 | 1.27 | 750 | 40 |  | 6.8
3 | Sosna i świerk (p.w.) |  | 0.04 | 0.16 | 10.2 | 2510 | 550 |  | 0.25
Condensation occurs inside partition!
Internal temperature: |  | 20 °C
Internal humidity: |  | 60 %
External temperature: |  | -10 °C
External humidity: |  | 90 %
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 36 -
Project: Thermal calculations of buildings
Partition definition name: |  | Dach b
Heat transfer coefficient: |  | 0,38 W/(m²·K)
Description: |  | Part of composite roof
Heat flow direction: |  | Up
Partition type: |  | Roof
Heat capt. res. (int.): |  | 0,100 (m²·K)/W
Heat capt. res. (ext.): |  | 0,040 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Płyty |  | 0.02 | 0.23 | 8.16 | 1000 | 1000 |  | 0.087
2 | Sosna i świerk (p.w.) |  | 0.34 | 0.16 | 10.2 | 2510 | 550 |  | 2.125
3 | Sosna i świerk (p.w.) |  | 0.04 | 0.16 | 10.2 | 2510 | 550 |  | 0.25
Condensation occurs inside partition!
Internal temperature: |  | 20 °C
Internal humidity: |  | 60 %
External temperature: |  | -10 °C
External humidity: |  | 90 %
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 37 -
Project: Thermal calculations of buildings
Partition definition name: |  | ExW 0.3(1)
Heat transfer coefficient: |  | 0,39 W/(m²·K)
Description: |  | External wall 0.3
Heat flow direction: |  | Horizontal
Partition type: |  | External wall
Heat capt. res. (int.): |  | 0,130 (m²·K)/W
Heat capt. res. (ext.): |  | 0,040 (m²·K)/W
No. | Type |  | d | λ | μ | Cp | ρ |  | R
|  |  | m | W/(m·K) | [−] | J/(kg·K) | kg/m³ |  | (m²·K)/W
1 | Tynk gipsowy |  | 0.01 | 0.35 | 0 | 1000 | 1000 |  | 0.029
2 | Styropian |  | 0.09 | 0.043 | 0 | 1460 | 1000 |  | 2.093
3 | Lekkie cegły |  | 0.2 | 0.8 | 0 | 1000 | 1000 |  | 0.25
Condensation occurs inside partition!
Internal temperature: |  | 20 °C
Internal humidity: |  | 60 %
External temperature: |  | -10 °C
External humidity: |  | 90 %
InstalSystem 5 ALPHA-ROOT (Rev. 2.0.A22) © InstalSoft 1996-2017 | [7 empty] | - 38 -