## Front page
Project
Project number: | 1 | Project version:
Description: | Tichelmann Installation System
Street:
Postal code and city: |  | Telephone:
Country: |  | Fax:
WWW:
E-mail:
Comment
Project developer
Name: | InstalSoft
Street:
Postal code and city: |  | Telephone:
Country: |  | Fax:
WWW:
E-mail:
VAT-id:
Comment
File info
File name: | C:\Users\misk\Documents\06-HS\SUZ-RH-BEZROZ-v5\InstalSoft-InstalSystem5-Tichelmann-Installation-System-modKMend.isproj
Program version: | 5.0 (Rev. 0.0.B30A1)
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  |  | - 1 -

## Components on pipe-runs
Project: Tichelmann Installation System
Components on pipe-runs
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (S) 1, Source: 1, m= 4731,6 kg/h, Diameter: 75 x 6,8 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 76 mm 70 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 2½"FT - 2"FT |  | 0.4 |  |  | 40
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee FT 75 - 2"FT - 75 |  |  |  |  | 0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 2½"FT |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 2½"FT |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 2½"FT |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 2½"FT |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
Pipe-run (R) 1, Source: 1, m= 4731,6 kg/h, Diameter: 75 x 6,8 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 76 mm 70 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 2½"FT - 2"FT |  | 0.4 |  |  | 39
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee FT 75 - 2"FT - 75 |  |  |  |  | 0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 2½"FT |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 2½"FT |  | 1.4 |  |  | 138
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 2 -

## Components on pipe-runs-1
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 2½"FT |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 2½"FT |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 25
Pipe-run (S) 10, Source: 1, m= 1639,0 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 30
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 10, Source: 1, m= 1639,0 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 30
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 11, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 284
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 11, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 283
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 3 -

## Components on pipe-runs-2
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 12, Source: 1, m= 1457,0 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 60
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 12, Source: 1, m= 1457,0 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 59
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 13, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 224
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 13, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 223
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 4 -

## Components on pipe-runs-3
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 14, Source: 1, m= 1274,8 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 47
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 14, Source: 1, m= 1274,8 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 47
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 15, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 172
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 15, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 171
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 5 -

## Components on pipe-runs-4
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (S) 16, Source: 1, m= 1092,7 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 36
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 16, Source: 1, m= 1092,7 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 36
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 17, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 126
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 17, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 126
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 18, Source: 1, m= 910,6 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 27
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 28
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 6 -

## Components on pipe-runs-5
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 40 - 1¼"MT |  | 0.3 |  |  | 28
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT 1¼"FT - 1¼"FT |  | 0.3 |  |  | 28
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 28
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  |  |  |  | 0
Pipe-run (R) 18, Source: 1, m= 910,6 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 26
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 28
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 40 - 1¼"MT |  | 0.3 |  |  | 28
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT 1¼"FT - 1¼"FT |  | 0.3 |  |  | 28
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 28
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  |  |  |  | 0
Pipe-run (S) 19, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 155
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 19, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 154
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 7 -

## Components on pipe-runs-6
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 2, Source: 1, m= 2367,5 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee FT 75 - 2"FT - 75 |  | 2.8 |  |  | 277
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 2"MT - 1¼"FT |  | 0.6 |  |  | 70
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (R) 2, Source: 1, m= 2367,5 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee FT 75 - 2"FT - 75 |  | 2.8 |  |  | 276
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 2"MT - 1¼"FT |  | 0.6 |  |  | 70
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (S) 20, Source: 1, m= 728,5 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 155
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 18
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 18
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  |  |  |  | 0
Pipe-run (R) 20, Source: 1, m= 728,5 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 154
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 18
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 18
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  |  |  |  | 0
Pipe-run (S) 21, Source: 1, m= 182,2 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 8 -

## Components on pipe-runs-7
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 99
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 21, Source: 1, m= 182,2 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 99
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 22, Source: 1, m= 546,4 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 99
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1"MT |  | 0.3 |  |  | 10
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 10
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  |  | 0
Pipe-run (R) 22, Source: 1, m= 546,4 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 99
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1"MT |  | 0.3 |  |  | 10
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 10
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 9 -

## Components on pipe-runs-8
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (S) 23, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2.8 |  |  | 111
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 23, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2.8 |  |  | 111
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 24, Source: 1, m= 364,3 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1.4 |  |  | 56
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 12
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 12
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  |  | 0
Pipe-run (R) 24, Source: 1, m= 364,3 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1.4 |  |  | 55
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 12
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 12
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 10 -

## Components on pipe-runs-9
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (S) 25, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2.8 |  |  | 135
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 25, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2.8 |  |  | 134
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 26, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1.4 |  |  | 67
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1"FT |  | 1.4 |  |  | 17
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 26, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 11 -

## Components on pipe-runs-10
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1.4 |  |  | 67
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1"FT |  | 1.4 |  |  | 17
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 27, Source: 1, m= 2364,1 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee FT 75 - 2"FT - 75 |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 32
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 2½"FT - 2"FT |  | 0.4 |  |  | 51
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 2"MT - 1¼"FT |  | 0.6 |  |  | 70
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1.4 |  |  | 177
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
Pipe-run (R) 27, Source: 1, m= 2364,1 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee FT 75 - 2"FT - 75 |  | 1.4 |  |  | 138
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 75 - 2½"MT |  | 0.3 |  |  | 32
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 2½"FT - 2"FT |  | 0.4 |  |  | 50
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 2"MT - 1¼"FT |  | 0.6 |  |  | 69
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
Pipe-run (R) 27_A, Source: 1, m= 2364,1 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 12 -

## Components on pipe-runs-11
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 2"MT - 1¼"FT |  | 0.6 |  |  | 69
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 2"FT - 2"FT - 2"FT |  |  |  |  | 0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1.4 |  |  | 177
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1.4 |  |  | 177
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 32
Pipe-run (S) 28, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 215
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 28, Source: 1, m= 2182,2 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 2"FT - 2"FT - 2"FT |  | 2.8 |  |  | 353
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 2"MT - 1¼"FT |  | 0.6 |  |  | 59
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 27
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (S) 29, Source: 1, m= 2182,2 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 51
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 13 -

## Components on pipe-runs-12
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (R) 29, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 183
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 3, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 216
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 3, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 215
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 14 -

## Components on pipe-runs-13
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 30, Source: 1, m= 2000,4 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 43
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (S) 30, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 183
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 31, Source: 1, m= 2000,4 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 43
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (R) 31, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 153
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 15 -

## Components on pipe-runs-14
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (R) 32, Source: 1, m= 1818,5 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 36
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT 1¼"FT - 1¼"FT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 40 - 1¼"MT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 32, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 154
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 33, Source: 1, m= 1818,5 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 36
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT 1¼"FT - 1¼"FT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 40 - 1¼"MT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 33, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 142
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 16 -

## Components on pipe-runs-15
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 34, Source: 1, m= 1636,6 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 30
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 34, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 142
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 35, Source: 1, m= 1636,7 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 30
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 35, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 282
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 17 -

## Components on pipe-runs-16
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 36, Source: 1, m= 1454,8 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 59
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 36, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 283
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 37, Source: 1, m= 1454,9 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 60
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 37, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 223
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 38, Source: 1, m= 1272,9 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 18 -

## Components on pipe-runs-17
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 47
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 38, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 224
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 39, Source: 1, m= 1273,0 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 47
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 39, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 170
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 4, Source: 1, m= 2185,3 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 51
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 19 -

## Components on pipe-runs-18
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (R) 4, Source: 1, m= 2185,3 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 51
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (R) 40, Source: 1, m= 1091,1 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 36
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 40, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 171
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 41, Source: 1, m= 1091,2 kg/h, Diameter: 40 x 3,7 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 42 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 36
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 41, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 125
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 20 -

## Components on pipe-runs-19
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (R) 42, Source: 1, m= 909,2 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 26
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 27
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 40 - 1¼"MT |  | 0.3 |  |  | 27
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT 1¼"FT - 1¼"FT |  | 0.3 |  |  | 27
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 27
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  |  |  |  | 0
Pipe-run (S) 42, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 126
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 43, Source: 1, m= 909,4 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 0.4 |  |  | 26
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 28
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 40 - 1¼"MT |  | 0.3 |  |  | 28
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT 1¼"FT - 1¼"FT |  | 0.3 |  |  | 28
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 28
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  |  |  |  | 0
Pipe-run (R) 43, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 154
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 21 -

## Components on pipe-runs-20
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 44, Source: 1, m= 727,4 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 154
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 18
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 18
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  |  |  |  | 0
Pipe-run (S) 44, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 154
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 45, Source: 1, m= 727,5 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 154
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 18
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 18
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  |  |  |  | 0
Pipe-run (R) 45, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 22 -

## Components on pipe-runs-21
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 98
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 46, Source: 1, m= 545,6 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 98
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1"MT |  | 0.3 |  |  | 10
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 10
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  |  | 0
Pipe-run (S) 46, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 99
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 47, Source: 1, m= 545,6 kg/h, Diameter: 32 x 2,9 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Tee 1¼"FT - 1"FT - 1¼"FT |  | 1.4 |  |  | 99
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1"MT |  | 0.3 |  |  | 10
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 32 - 1¼"MT |  | 0.3 |  |  | 10
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 23 -

## Components on pipe-runs-22
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (R) 47, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2.8 |  |  | 111
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 48, Source: 1, m= 363,7 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1.4 |  |  | 55
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 12
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 12
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  |  | 0
Pipe-run (S) 48, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2.8 |  |  | 111
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 49, Source: 1, m= 363,7 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1.4 |  |  | 56
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 12
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 12
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 24 -

## Components on pipe-runs-23
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (R) 49, Source: 1, m= 181,8 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2.8 |  |  | 134
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 5, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 184
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 5, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 183
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 25 -

## Components on pipe-runs-24
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
Pipe-run (R) 50, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1.4 |  |  | 67
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1"FT |  | 1.4 |  |  | 17
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 50, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2.8 |  |  | 134
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 51, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 2"FT - 2"FT - 2"FT |  | 1.4 |  |  | 177
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 2"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 51, Source: 1, m= 181,9 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 26 -

## Components on pipe-runs-25
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1.4 |  |  | 67
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1"FT |  | 1.4 |  |  | 17
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 6, Source: 1, m= 2003,2 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 43
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (R) 6, Source: 1, m= 2003,2 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 43
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  |  |  |  | 0
Pipe-run (S) 7, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 155
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 7, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 1.7 |  |  | 154
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 27 -

## Components on pipe-runs-26
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT-MT 1¼"MT - 1"FT |  | 0.6 |  |  | 7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (S) 8, Source: 1, m= 1821,1 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 36
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT 1¼"FT - 1¼"FT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 40 - 1¼"MT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (R) 8, Source: 1, m= 1821,1 kg/h, Diameter: 50 x 4,6 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 54 mm 50 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 50 - 1¼"FT - 50 |  | 0.4 |  |  | 36
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 50 - 1¼"MT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Connection FT 1¼"FT - 1¼"FT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 40 - 1¼"MT |  | 0.3 |  |  | 19
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  |  |  |  | 0
Pipe-run (S) 9, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 143
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 28 -

## Components on pipe-runs-27
Project: Tichelmann Installation System
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Thermal resistance
[5 empty] | m³/h |  | Pa
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
Pipe-run (R) 9, Source: 1, m= 182,1 kg/h, Diameter: 25 x 2,3 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 25 mm 25 mm
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction tee PN6 40 - 1"FT - 40 |  | 1.9 |  |  | 142
| PEX (pipes and fittings) acc. to EN ISO 15875 | Adapter PN6 25 - 1"MT |  | 0.3 |  |  | 3
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
| NONE | Elbow on drawing |  | 0.7 |  |  | 8
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 29 -

## General results heating
Project: Tichelmann Installation System
General results heating
No. of sources |  |  | 1
Total number of terminal units |  |  | 26
Total number of pipe-runs |  |  | 107
Total number of manifolds |  |  | 0
Total number of pumps |  |  | 0
Spec. total rooms heat loss ΦH |  |  | 233664 |  | W
Spec. total req. heat output of other TU's |  |  | 0 |  | W
Spec. total rooms req. heat output Φreq |  |  | 233664 |  | W
Calculation standards:
Radiators sizing standard |  |  | EN 442-2
Floor heating standard |  |  | EN 1264-1,2,3:1999, EN 1264-4:2003
Wall and ceiling panels calculation standard |  |  | EN 14037
Source: Plate type exchanger: 1, Application: Heating systems, Medium: Water
| Source elevation |  | 0.8 |  | m
| Supply and return temperature |  | 30,0 / 19,0 |  | °C
| Total output |  | 60551 |  | W
| Total output of convectors Φconv,H |  | 0 |  | W
| Total output of radiant heaters Φrh,H |  | 51767 |  | W
| Total output of other heaters |  | 0 |  | W
| Heat gains from pipe-runs accounted for in balance |  | 44 |  | W
| Not utilized heat loss of pipe-runs |  | 386 |  | W
| Losses of radiant systems to outside of source feed area |  | 8355 |  | W
| Losses of radiant systems within source feed area |  | 0 |  | W
| Available pressure |  | 23.3 |  | kPa
| Pressure drop along critical route |  | 23.3 |  | kPa
| Pressure drop on critical terminal unit |  | 5.8 |  | kPa
| Press. drop on source |  | 0 |  | kPa
| Flow rate in source |  | 4731.6 |  | kg/h
| Critical receptor: | Tennis court-1-12
| Critical TU route length |  | 184.9 |  | m
| Capacity of system incl. terminal units |  | 2496.3 |  | dm³
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  |  |  | - 30 -

## Radiant heating general res
Project: Tichelmann Installation System
Radiant heating general results
Source/Source: 1 |  |  | Application: Heating systems |  | Medium: Water
Temperatures θs,H and θr,H [°C] |  | 30 |  | 19
Temperature source for control circuits | Source/1
Temperatures θs,H and θr,H [°C] |  | 30 |  | 19
Required heating output Φreq,H [W] |  | 51767
Obtained heating output ΦH [W] |  | 51767
Heat capacity lost ΦOS,H [W] |  | 8355
Mass flow rate m [kg/h] |  | 4731.6
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [5 empty] | - 31 -

## Detailed radiant heating re
Project: Tichelmann Installation System
Detailed radiant heating results
Heating/cooling zone symbol |  | Area | Occupied / peripheral zone | Surface temperature |  | Thermal resistance of covering |  | Required output of heating |  | Output gained |  | Output lost |  | Unit power |  | Pipe spacing |  | Temp. diff. supply-return |  | Area occupied by passing feeds |  | Heating power from passing feeds |  | Length of circuit feeds |  | Overall circuit length (feeds + loop) |  | Mass flow rate |  | Flow velocity |  | Pressure loss in circuit |  | Pressure drop on regulating valves |  | Total pressure loss |  | Valve setting
H/C Area |  | A | Type | θfloor,H |  | Rλ,B |  | Φreq,H |  | ΦH |  | ΦOS,H |  | qH |  | VA |  | ΔθH |  | Afeed |  | Φfeeds,H |  | Lfeeds |  | Ltot |  | m |  | v |  | Δp |  | Δpreg,s Δpreg,p |  | Δptot |  | n
|  | m² |  | °C |  | (m²·K)/W |  | W |  | W |  | W |  | W/m² |  | mm |  | K |  | m² |  | W |  | m |  | m |  | kg/h |  | m/s |  | kPa |  | kPa |  | kPa
Areas supplied with no manifold. Source: 1; Storey: 0, Tennis court; Bld. unit: 01; θs,H: 30,0;
Room: Tennis court; θi,H: 16,0 °C; Φreq,H: 51767 W; Φ surplus: 0 W;
| Tennis court-1-1 | 49.7 | OZ | 19.9 | 0.02 |  | 1990 |  | 1990 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.9 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-2 | 49.7 | OZ | 19.9 | 0.02 |  | 1990 |  | 1990 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.9 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-3 | 49.7 | OZ | 19.9 | 0.02 |  | 1990 |  | 1990 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.9 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-4 | 49.8 | OZ | 19.9 | 0.02 |  | 1990 |  | 1990 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.8 |  | 181.9 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-5 | 49.7 | OZ | 19.9 | 0.02 |  | 1990 |  | 1990 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.8 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-6 | 49.7 | OZ | 19.9 | 0.02 |  | 1989 |  | 1989 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.8 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-7 | 49.7 | OZ | 19.9 | 0.02 |  | 1989 |  | 1989 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.8 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-8 | 49.7 | OZ | 19.9 | 0.02 |  | 1990 |  | 1990 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.9 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-9 | 49.7 | OZ | 19.9 | 0.02 |  | 1989 |  | 1989 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.8 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-10 | 49.7 | OZ | 19.9 | 0.02 |  | 1989 |  | 1989 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.8 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [36 empty] | - 32 -

## Detailed radiant heating re-1
Project: Tichelmann Installation System
H/C Area |  | A | Type | θfloor,H |  | Rλ,B |  | Φreq,H |  | ΦH |  | ΦOS,H |  | qH |  | VA |  | ΔθH |  | Afeed |  | Φfeeds,H |  | Lfeeds |  | Ltot |  | m |  | v |  | Δp |  | Δpreg,s Δpreg,p |  | Δptot |  | n
|  | m² |  | °C |  | (m²·K)/W |  | W |  | W |  | W |  | W/m² |  | mm |  | K |  | m² |  | W |  | m |  | m |  | kg/h |  | m/s |  | kPa |  | kPa |  | kPa
| Tennis court-1-11 | 49.7 | OZ | 19.9 | 0.02 |  | 1990 |  | 1990 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.9 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-12 | 49.7 | OZ | 19.9 | 0.02 |  | 1989 |  | 1989 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.8 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-1-13 | 49.7 | OZ | 19.9 | 0.02 |  | 1990 |  | 1990 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 248.7 |  | 181.9 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-1 | 49.8 | OZ | 19.9 | 0.02 |  | 1993 |  | 1993 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249.1 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-2 | 49.8 | OZ | 19.9 | 0.02 |  | 1993 |  | 1993 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249.1 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-3 | 49.8 | OZ | 19.9 | 0.02 |  | 1992 |  | 1992 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249.1 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-4 | 49.8 | OZ | 19.9 | 0.02 |  | 1993 |  | 1993 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249.1 |  | 182.2 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-5 | 49.8 | OZ | 19.9 | 0.02 |  | 1992 |  | 1992 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-6 | 49.8 | OZ | 19.9 | 0.02 |  | 1992 |  | 1992 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-7 | 49.8 | OZ | 19.9 | 0.02 |  | 1992 |  | 1992 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-8 | 49.8 | OZ | 19.9 | 0.02 |  | 1993 |  | 1993 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249.1 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-9 | 49.8 | OZ | 19.9 | 0.02 |  | 1992 |  | 1992 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-10 | 49.8 | OZ | 19.9 | 0.02 |  | 1992 |  | 1992 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-11 | 49.8 | OZ | 19.9 | 0.02 |  | 1993 |  | 1993 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249.1 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-12 | 49.8 | OZ | 19.9 | 0.02 |  | 1992 |  | 1992 |  | 321 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
| Tennis court-2-13 | 49.8 | OZ | 19.9 | 0.02 |  | 1993 |  | 1993 |  | 322 |  | 40 |  | 200 |  | 11 |  | 0 |  | 0 |  | 0 |  | 249.1 |  | 182.1 |  | 0.15 |  | 5.8 |  | 0,0 0,0 |  | 5.8
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [36 empty] | - 33 -

## Heating pipe-runs
Project: Tichelmann Installation System
Heating pipe-runs
Pipe-run type |  | Pipe-run no. |  | Connection piperun No. | Heat quantity carried by pipe-run | Diameter | Length | Specific friction resistance | Total friction loss | Total loss | Flow velocity | Mass flow rate | Insulation thickness | Inlet temperature | Specific heat loss in pipe-run
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm | °C | W/m
Source: |  |  | 1
| S | 1 |  | Source: 1 | 60121 | 75 x 6,8 | 21.12 | 37 | 8.3 | 1588 | 0.45 | 4731.6 | 70 | 30 | 2.79
| R | 1 |  | Source: 1 | 60121 | 75 x 6,8 | 19.72 | 39 | 8.3 | 1574 | 0.44 | 4731.6 | 70 | 19 | 0.56
| S | 2 |  | 1 | 30082 | 50 x 4,6 | 0.53 | 75 | 3.6 | 418 | 0.5 | 2367.5 | 50 | 30 | 2.6
| R | 2 |  | 1 | 30082 | 50 x 4,6 | 2.96 | 80 | 3.6 | 613 | 0.5 | 2367.5 | 50 | 19 | 0.52
| S | 3 |  | 2 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.9 | 251 | 0.16 | 182.1 | 25 | 30 | 2.39
| R | 3 |  | 2 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.9 | 248 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 4 |  | 2 | 27768 | 50 x 4,6 | 2.79 | 65 | 0.4 | 233 | 0.47 | 2185.3 | 50 | 30 | 2.6
| R | 4 |  | 2 | 27768 | 50 x 4,6 | 2.79 | 69 | 0.4 | 244 | 0.46 | 2185.3 | 50 | 19 | 0.52
| S | 5 |  | 4 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.9 | 219 | 0.16 | 182.1 | 25 | 30 | 2.39
| R | 5 |  | 4 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.9 | 217 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 6 |  | 4 | 25454 | 50 x 4,6 | 2.77 | 56 | 0.4 | 199 | 0.43 | 2003.2 | 50 | 30 | 2.6
| R | 6 |  | 4 | 25454 | 50 x 4,6 | 2.77 | 59 | 0.4 | 207 | 0.43 | 2003.2 | 50 | 19 | 0.52
| S | 7 |  | 6 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.9 | 190 | 0.16 | 182.1 | 25 | 30 | 2.39
| R | 7 |  | 6 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.9 | 187 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 8 |  | 6 | 23140 | 50 x 4,6 | 2.77 | 47 | 1.2 | 224 | 0.39 | 1821.1 | 50 | 30 | 2.6
| R | 8 |  | 6 | 23140 | 50 x 4,6 | 2.77 | 50 | 1.2 | 231 | 0.39 | 1821.1 | 50 | 19 | 0.52
| S | 9 |  | 8 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.6 | 171 | 0.16 | 182.1 | 25 | 30 | 2.39
| R | 9 |  | 8 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.6 | 169 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 10 |  | 8 | 20826 | 40 x 3,7 | 2.77 | 115 | 0.4 | 347 | 0.55 | 1639 | 40 | 30 | 2.53
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 34 -

## Heating pipe-runs-1
Project: Tichelmann Installation System
Type |  | Pipe-run symbol | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. | θinlet,H | qH
|  |  |  | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm | °C | W/m
| R | 10 | 8 | 20826 | 40 x 3,7 | 2.77 | 121 | 0.4 | 366 | 0.55 | 1639 | 40 | 19 | 0.5
| S | 11 | 10 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.6 | 312 | 0.16 | 182.1 | 25 | 30 | 2.39
| R | 11 | 10 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.6 | 309 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 12 | 10 | 18513 | 40 x 3,7 | 2.77 | 93 | 0.4 | 318 | 0.49 | 1457 | 40 | 30 | 2.53
| R | 12 | 10 | 18513 | 40 x 3,7 | 2.77 | 99 | 0.4 | 332 | 0.48 | 1457 | 40 | 19 | 0.5
| S | 13 | 12 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.6 | 253 | 0.16 | 182.1 | 25 | 30 | 2.39
| R | 13 | 12 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.6 | 250 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 14 | 12 | 16198 | 40 x 3,7 | 2.77 | 74 | 0.4 | 251 | 0.43 | 1274.8 | 40 | 30 | 2.53
| R | 14 | 12 | 16198 | 40 x 3,7 | 2.77 | 78 | 0.4 | 263 | 0.42 | 1274.8 | 40 | 19 | 0.5
| S | 15 | 14 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.6 | 200 | 0.16 | 182.1 | 25 | 30 | 2.39
| R | 15 | 14 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.6 | 198 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 16 | 14 | 13885 | 40 x 3,7 | 2.77 | 56 | 0.4 | 192 | 0.37 | 1092.7 | 40 | 30 | 2.53
| R | 16 | 14 | 13885 | 40 x 3,7 | 2.77 | 60 | 0.4 | 201 | 0.36 | 1092.7 | 40 | 19 | 0.5
| S | 17 | 16 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.6 | 155 | 0.16 | 182.1 | 25 | 30 | 2.38
| R | 17 | 16 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.6 | 152 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 18 | 16 | 11571 | 32 x 2,9 | 2.77 | 115 | 1.4 | 456 | 0.47 | 910.6 | 40 | 30 | 2.25
| R | 18 | 16 | 11571 | 32 x 2,9 | 2.77 | 122 | 1.4 | 475 | 0.47 | 910.6 | 40 | 19 | 0.45
| S | 19 | 18 | 2314 | 25 x 2,3 | 0.39 | 23 | 3.1 | 183 | 0.16 | 182.1 | 25 | 30 | 2.38
| R | 19 | 18 | 2314 | 25 x 2,3 | 0.3 | 24 | 3.1 | 181 | 0.15 | 182.1 | 25 | 19 | 0.47
| S | 20 | 18 | 9257 | 32 x 2,9 | 2.77 | 78 | 1.9 | 406 | 0.38 | 728.5 | 40 | 30 | 2.25
| R | 20 | 18 | 9257 | 32 x 2,9 | 2.77 | 83 | 1.9 | 418 | 0.38 | 728.5 | 40 | 19 | 0.45
| S | 21 | 20 | 2315 | 25 x 2,3 | 0.39 | 23 | 3.1 | 128 | 0.16 | 182.2 | 25 | 29.9 | 2.38
| R | 21 | 20 | 2315 | 25 x 2,3 | 0.3 | 24 | 3.1 | 126 | 0.15 | 182.2 | 25 | 19 | 0.47
| S | 22 | 20 | 6943 | 32 x 2,9 | 2.77 | 47 | 1.9 | 249 | 0.28 | 546.4 | 40 | 29.9 | 2.25
| R | 22 | 20 | 6943 | 32 x 2,9 | 2.77 | 50 | 1.9 | 257 | 0.28 | 546.4 | 40 | 18.9 | 0.45
| S | 23 | 22 | 2314 | 25 x 2,3 | 0.39 | 23 | 4.5 | 140 | 0.16 | 182.1 | 25 | 29.9 | 2.38
| R | 23 | 22 | 2314 | 25 x 2,3 | 0.3 | 24 | 4.5 | 138 | 0.15 | 182.1 | 25 | 19 | 0.47
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [12 empty] | - 35 -

## Heating pipe-runs-2
Project: Tichelmann Installation System
Type |  | Pipe-run symbol | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. | θinlet,H | qH
|  |  |  | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm | °C | W/m
| S | 24 | 22 | 4628 | 25 x 2,3 | 2.77 | 76 | 1.9 | 290 | 0.31 | 364.3 | 25 | 29.9 | 2.38
| R | 24 | 22 | 4628 | 25 x 2,3 | 2.77 | 81 | 1.9 | 303 | 0.31 | 364.3 | 25 | 18.9 | 0.46
| S | 25 | 24 | 2314 | 25 x 2,3 | 0.39 | 23 | 4.5 | 163 | 0.16 | 182.1 | 25 | 29.9 | 2.38
| R | 25 | 24 | 2314 | 25 x 2,3 | 0.3 | 24 | 4.5 | 161 | 0.15 | 182.1 | 25 | 19 | 0.46
| S | 26 | 24 | 2314 | 25 x 2,3 | 2.84 | 23 | 4.3 | 166 | 0.16 | 182.1 | 25 | 29.9 | 2.38
| R | 26 | 24 | 2314 | 25 x 2,3 | 2.84 | 24 | 4.3 | 169 | 0.15 | 182.1 | 25 | 18.9 | 0.46
| S | 26_A | 26 | 2314 | 25 x 2,3 | 0.25 | 23 | 0 | 6 | 0.16 | 182.1 | 25 | 29.9 | 2.37
| R | 26_A | 26 | 2314 | 25 x 2,3 | 0.15 | 24 | 0 | 4 | 0.15 | 182.1 | 25 | 18.9 | 0.46
| S | 27 | 1 | 30039 | 50 x 4,6 | 37.12 | 75 | 4.8 | 3354 | 0.5 | 2364.1 | 50 | 30 | 2.59
| R | 27 | 1 | 30039 | 50 x 4,6 | 36.51 | 80 | 2.9 | 3223 | 0.5 | 2364.1 | 50 | 18.9 | 0.51
| R | 27_A | 27 | 30039 | 50 x 4,6 | 36.37 | 80 | 4.6 | 3472 | 0.5 | 2364.1 | 50 | 19 | 0.52
| S | 28 | 27 | 2311 | 25 x 2,3 | 0.38 | 23 | 3.9 | 250 | 0.16 | 181.9 | 25 | 30 | 2.38
| R | 28 | 27_A | 27729 | 50 x 4,6 | 2.76 | 69 | 3.6 | 630 | 0.46 | 2182.2 | 50 | 19 | 0.52
| S | 29 | 27 | 27728 | 50 x 4,6 | 2.74 | 65 | 0.4 | 230 | 0.47 | 2182.2 | 50 | 30 | 2.59
| R | 29 | 28 | 2311 | 25 x 2,3 | 0.49 | 24 | 3.9 | 221 | 0.15 | 181.9 | 25 | 18.9 | 0.46
| R | 30 | 28 | 25418 | 50 x 4,6 | 2.76 | 59 | 0.4 | 207 | 0.42 | 2000.4 | 50 | 19 | 0.52
| S | 30 | 29 | 2310 | 25 x 2,3 | 0.38 | 23 | 3.9 | 218 | 0.16 | 181.8 | 25 | 30 | 2.38
| S | 31 | 29 | 25418 | 50 x 4,6 | 2.76 | 56 | 0.4 | 198 | 0.43 | 2000.4 | 50 | 30 | 2.59
| R | 31 | 30 | 2311 | 25 x 2,3 | 0.49 | 24 | 3.9 | 192 | 0.15 | 181.9 | 25 | 18.9 | 0.46
| R | 32 | 30 | 23107 | 50 x 4,6 | 2.76 | 50 | 1.2 | 231 | 0.39 | 1818.5 | 50 | 19 | 0.52
| S | 32 | 31 | 2311 | 25 x 2,3 | 0.38 | 23 | 3.9 | 189 | 0.16 | 181.9 | 25 | 29.9 | 2.38
| S | 33 | 31 | 23107 | 50 x 4,6 | 2.76 | 47 | 1.2 | 223 | 0.39 | 1818.5 | 50 | 29.9 | 2.59
| R | 33 | 32 | 2311 | 25 x 2,3 | 0.49 | 24 | 3.6 | 173 | 0.15 | 181.9 | 25 | 19 | 0.46
| R | 34 | 32 | 20795 | 40 x 3,7 | 2.76 | 121 | 0.4 | 364 | 0.54 | 1636.6 | 40 | 19 | 0.5
| S | 34 | 33 | 2310 | 25 x 2,3 | 0.38 | 23 | 3.6 | 171 | 0.16 | 181.8 | 25 | 29.9 | 2.38
| S | 35 | 33 | 20797 | 40 x 3,7 | 2.76 | 114 | 0.4 | 346 | 0.55 | 1636.7 | 40 | 29.9 | 2.53
| R | 35 | 34 | 2311 | 25 x 2,3 | 0.49 | 24 | 3.6 | 313 | 0.15 | 181.8 | 25 | 19 | 0.46
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [12 empty] | - 36 -

## Heating pipe-runs-3
Project: Tichelmann Installation System
Type |  | Pipe-run symbol | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. | θinlet,H | qH
|  |  |  | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm | °C | W/m
| R | 36 | 34 | 18485 | 40 x 3,7 | 2.76 | 98 | 0.4 | 331 | 0.48 | 1454.8 | 40 | 19 | 0.5
| S | 36 | 35 | 2310 | 25 x 2,3 | 0.38 | 23 | 3.6 | 311 | 0.16 | 181.8 | 25 | 29.9 | 2.38
| S | 37 | 35 | 18487 | 40 x 3,7 | 2.76 | 93 | 0.4 | 316 | 0.49 | 1454.9 | 40 | 29.9 | 2.53
| R | 37 | 36 | 2311 | 25 x 2,3 | 0.49 | 24 | 3.6 | 254 | 0.15 | 181.8 | 25 | 19 | 0.46
| R | 38 | 36 | 16174 | 40 x 3,7 | 2.76 | 78 | 0.4 | 262 | 0.42 | 1272.9 | 40 | 19 | 0.5
| S | 38 | 37 | 2311 | 25 x 2,3 | 0.38 | 23 | 3.6 | 252 | 0.16 | 181.9 | 25 | 29.9 | 2.38
| S | 39 | 37 | 16176 | 40 x 3,7 | 2.76 | 74 | 0.4 | 250 | 0.43 | 1273 | 40 | 29.9 | 2.53
| R | 39 | 38 | 2310 | 25 x 2,3 | 0.49 | 24 | 3.6 | 202 | 0.15 | 181.8 | 25 | 19 | 0.46
| R | 40 | 38 | 13864 | 40 x 3,7 | 2.76 | 59 | 0.4 | 200 | 0.36 | 1091.1 | 40 | 19 | 0.5
| S | 40 | 39 | 2310 | 25 x 2,3 | 0.38 | 23 | 3.6 | 200 | 0.16 | 181.8 | 25 | 29.9 | 2.38
| S | 41 | 39 | 13865 | 40 x 3,7 | 2.76 | 56 | 0.4 | 191 | 0.36 | 1091.2 | 40 | 29.9 | 2.53
| R | 41 | 40 | 2311 | 25 x 2,3 | 0.49 | 24 | 3.6 | 157 | 0.15 | 181.9 | 25 | 19 | 0.47
| R | 42 | 40 | 11553 | 32 x 2,9 | 2.76 | 122 | 1.4 | 473 | 0.47 | 909.2 | 40 | 19 | 0.45
| S | 42 | 41 | 2311 | 25 x 2,3 | 0.38 | 23 | 3.6 | 154 | 0.16 | 181.8 | 25 | 29.9 | 2.38
| S | 43 | 41 | 11555 | 32 x 2,9 | 2.76 | 115 | 1.4 | 455 | 0.47 | 909.4 | 40 | 29.9 | 2.24
| R | 43 | 42 | 2310 | 25 x 2,3 | 0.49 | 24 | 3.1 | 185 | 0.15 | 181.8 | 25 | 19 | 0.47
| R | 44 | 42 | 9243 | 32 x 2,9 | 2.76 | 82 | 1.9 | 416 | 0.37 | 727.4 | 40 | 19 | 0.45
| S | 44 | 43 | 2311 | 25 x 2,3 | 0.38 | 23 | 3.1 | 183 | 0.16 | 181.8 | 25 | 29.9 | 2.38
| S | 45 | 43 | 9244 | 32 x 2,9 | 2.76 | 78 | 1.9 | 404 | 0.38 | 727.5 | 40 | 29.9 | 2.24
| R | 45 | 44 | 2310 | 25 x 2,3 | 0.49 | 24 | 3.1 | 130 | 0.15 | 181.8 | 25 | 19 | 0.47
| R | 46 | 44 | 6932 | 32 x 2,9 | 2.76 | 50 | 1.9 | 256 | 0.28 | 545.6 | 40 | 19 | 0.45
| S | 46 | 45 | 2311 | 25 x 2,3 | 0.38 | 23 | 3.1 | 127 | 0.16 | 181.9 | 25 | 29.9 | 2.38
| S | 47 | 45 | 6933 | 32 x 2,9 | 2.76 | 47 | 1.9 | 248 | 0.28 | 545.6 | 40 | 29.9 | 2.24
| R | 47 | 46 | 2311 | 25 x 2,3 | 0.49 | 24 | 4.5 | 142 | 0.15 | 181.9 | 25 | 19 | 0.47
| R | 48 | 46 | 4621 | 25 x 2,3 | 2.76 | 80 | 1.9 | 301 | 0.31 | 363.7 | 25 | 19 | 0.47
| S | 48 | 47 | 2311 | 25 x 2,3 | 0.38 | 23 | 4.5 | 139 | 0.16 | 181.9 | 25 | 29.9 | 2.37
| S | 49 | 47 | 4622 | 25 x 2,3 | 2.76 | 76 | 1.9 | 289 | 0.31 | 363.7 | 25 | 29.9 | 2.37
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [12 empty] | - 37 -

## Heating pipe-runs-4
Project: Tichelmann Installation System
Type |  | Pipe-run symbol | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. | θinlet,H | qH
|  |  |  | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm | °C | W/m
| R | 49 | 48 | 2310 | 25 x 2,3 | 0.49 | 24 | 4.5 | 165 | 0.15 | 181.8 | 25 | 19 | 0.47
| R | 50 | 48 | 2311 | 25 x 2,3 | 2.81 | 24 | 4.3 | 168 | 0.15 | 181.9 | 25 | 19 | 0.47
| S | 50 | 49 | 2311 | 25 x 2,3 | 0.38 | 23 | 4.5 | 163 | 0.16 | 181.9 | 25 | 29.9 | 2.37
| R | 50_A | 50 | 2311 | 25 x 2,3 | 0.35 | 24 | 0 | 8 | 0.15 | 181.9 | 25 | 19 | 0.47
| R | 51 | 27_A | 2311 | 25 x 2,3 | 0.49 | 24 | 3.6 | 215 | 0.15 | 181.9 | 25 | 18.9 | 0.45
| S | 51 | 49 | 2311 | 25 x 2,3 | 2.83 | 23 | 4.3 | 165 | 0.16 | 181.9 | 25 | 29.9 | 2.37
| S | 51_A | 51 | 2311 | 25 x 2,3 | 0.24 | 23 | 0 | 5 | 0.16 | 181.9 | 25 | 29.9 | 2.37
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [12 empty] | - 38 -

## List of rooms - heating
Project: Tichelmann Installation System
List of rooms - heating
Room Symbol |  |  |  |  | Room surface area | Thermal resistance of covering |  | Design room temperature | Heat loss in room | Required output of heating | Required specific heating output | Required radiant heating output | Required convection heating output | Obtained radiant heating output | Obtained convection heating output | Output recovered from pipe-runs | Coverage of required heating output
Room |  |  |  |  | A | Rλ,B |  | θi,H | Φstd,H | Φreq,H | qreq,H | Φreq,rad,H | Φreq,conv,H | Φrh,H | Φconv,H | Φpipe,H | %Φreq,H
[5 empty] | m² | (m²·K)/W |  | °C | W | W | W/m² | W | W | W | W | W | %
Storey: |  | 0, | Elevation |  |  |  | 0 m
| Bld. unit: |  |  | 01
| 0-09 |  |  |  | 28.2 |  |  | 16 | 1128 | 1128 | 40 | 0 | 1128 | 0 | 0 | 0 | 0
| Tennis court |  |  |  | 1294.2 | 0.02 |  | 16 | 51767 | 51767 | 40 | 51767 | 0 | 51767 | 0 | 43.94 | 100
| U3.1. Tennis hall |  |  |  | 2583.4 |  |  | 16 | 103335 | 103335 | 40 | 0 | 103335 | 0 | 0 | 0 | 0
| U4.1. Tennis hall |  |  |  | 1935.9 |  |  | 16 | 77435 | 77435 | 40 | 0 | 77435 | 0 | 0 | 0 | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [15 empty] | - 39 -

## Heating_cooling circuits
Project: Tichelmann Installation System
Heating/cooling circuits
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-12
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 30 | 2310 |  | 181.8 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.9 | 210 | 218 | 0 |  | 218 | 25
| Heating/cooling floor | Tennis court-1-12 | 1989 |  | 181.8 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5781
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 49 | 2310 |  | 181.8 | 25 x 2,3 | 0.49 | 0.15 | 24 | 4.5 | 153 | 165 | 0 |  | 165 | 25
|  | 48 | 4621 |  | 363.7 | 25 x 2,3 | 2.76 | 0.31 | 80 | 1.9 | 79 | 301 | 0 |  | 301 | 25
|  | 46 | 6932 |  | 545.6 | 32 x 2,9 | 2.76 | 0.28 | 50 | 1.9 | 118 | 256 | 0 |  | 256 | 40
|  | 44 | 9243 |  | 727.4 | 32 x 2,9 | 2.76 | 0.37 | 82 | 1.9 | 189 | 416 | 0 |  | 416 | 40
|  | 42 | 11553 |  | 909.2 | 32 x 2,9 | 2.76 | 0.47 | 122 | 1.4 | 136 | 473 | 0 |  | 473 | 40
|  | 40 | 13864 |  | 1091.1 | 40 x 3,7 | 2.76 | 0.36 | 59 | 0.4 | 36 | 200 | 0 |  | 200 | 40
|  | 38 | 16174 |  | 1272.9 | 40 x 3,7 | 2.76 | 0.42 | 78 | 0.4 | 47 | 262 | 0 |  | 262 | 40
|  | 36 | 18485 |  | 1454.8 | 40 x 3,7 | 2.76 | 0.48 | 98 | 0.4 | 59 | 331 | 0 |  | 331 | 40
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | 0
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-9
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 36 | 2310 |  | 181.8 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.6 | 303 | 311 | 0 |  | 311 | 25
| Heating/cooling floor | Tennis court-1-9 | 1989 |  | 181.8 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5782
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 43 | 2310 |  | 181.8 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.1 | 173 | 185 | 0 |  | 185 | 25
|  | 42 | 11553 |  | 909.2 | 32 x 2,9 | 2.76 | 0.47 | 122 | 1.4 | 136 | 473 | 0 |  | 473 | 40
|  | 40 | 13864 |  | 1091.1 | 40 x 3,7 | 2.76 | 0.36 | 59 | 0.4 | 36 | 200 | 0 |  | 200 | 40
|  | 38 | 16174 |  | 1272.9 | 40 x 3,7 | 2.76 | 0.42 | 78 | 0.4 | 47 | 262 | 0 |  | 262 | 40
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 40 -

## Heating_cooling circuits-1
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 36 | 18485 |  | 1454.8 | 40 x 3,7 | 2.76 | 0.48 | 98 | 0.4 | 59 | 331 | 0 |  | 331 | 40
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -92
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-2
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 37 | 18487 |  | 1454.9 | 40 x 3,7 | 2.76 | 0.49 | 93 | 0.4 | 60 | 316 | 0 |  | 316 | 40
|  | 39 | 16176 |  | 1273 | 40 x 3,7 | 2.76 | 0.43 | 74 | 0.4 | 47 | 250 | 0 |  | 250 | 40
|  | 41 | 13865 |  | 1091.2 | 40 x 3,7 | 2.76 | 0.36 | 56 | 0.4 | 36 | 191 | 0 |  | 191 | 40
|  | 43 | 11555 |  | 909.4 | 32 x 2,9 | 2.76 | 0.47 | 115 | 1.4 | 137 | 455 | 0 |  | 455 | 40
|  | 45 | 9244 |  | 727.5 | 32 x 2,9 | 2.76 | 0.38 | 78 | 1.9 | 190 | 404 | 0 |  | 404 | 40
|  | 47 | 6933 |  | 545.6 | 32 x 2,9 | 2.76 | 0.28 | 47 | 1.9 | 119 | 248 | 0 |  | 248 | 40
|  | 49 | 4622 |  | 363.7 | 25 x 2,3 | 2.76 | 0.31 | 76 | 1.9 | 80 | 289 | 0 |  | 289 | 25
|  | 50 | 2311 |  | 181.9 | 25 x 2,3 | 0.38 | 0.16 | 23 | 4.5 | 154 | 163 | 0 |  | 163 | 25
| Heating/cooling floor | Tennis court-1-2 | 1990 |  | 181.9 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5786
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 29 | 2311 |  | 181.9 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.9 | 209 | 221 | 0 |  | 221 | 25
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -114
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-5
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 37 | 18487 |  | 1454.9 | 40 x 3,7 | 2.76 | 0.49 | 93 | 0.4 | 60 | 316 | 0 |  | 316 | 40
|  | 39 | 16176 |  | 1273 | 40 x 3,7 | 2.76 | 0.43 | 74 | 0.4 | 47 | 250 | 0 |  | 250 | 40
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 41 -

## Heating_cooling circuits-2
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 41 | 13865 |  | 1091.2 | 40 x 3,7 | 2.76 | 0.36 | 56 | 0.4 | 36 | 191 | 0 |  | 191 | 40
|  | 43 | 11555 |  | 909.4 | 32 x 2,9 | 2.76 | 0.47 | 115 | 1.4 | 137 | 455 | 0 |  | 455 | 40
|  | 44 | 2311 |  | 181.8 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.1 | 174 | 183 | 0 |  | 183 | 25
| Heating/cooling floor | Tennis court-1-5 | 1990 |  | 181.8 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5784
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 35 | 2311 |  | 181.8 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.6 | 301 | 313 | 0 |  | 313 | 25
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -144
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-11
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 32 | 2311 |  | 181.9 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.9 | 181 | 189 | 0 |  | 189 | 25
| Heating/cooling floor | Tennis court-1-11 | 1990 |  | 181.9 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5786
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 47 | 2311 |  | 181.9 | 25 x 2,3 | 0.49 | 0.15 | 24 | 4.5 | 130 | 142 | 0 |  | 142 | 25
|  | 46 | 6932 |  | 545.6 | 32 x 2,9 | 2.76 | 0.28 | 50 | 1.9 | 118 | 256 | 0 |  | 256 | 40
|  | 44 | 9243 |  | 727.4 | 32 x 2,9 | 2.76 | 0.37 | 82 | 1.9 | 189 | 416 | 0 |  | 416 | 40
|  | 42 | 11553 |  | 909.2 | 32 x 2,9 | 2.76 | 0.47 | 122 | 1.4 | 136 | 473 | 0 |  | 473 | 40
|  | 40 | 13864 |  | 1091.1 | 40 x 3,7 | 2.76 | 0.36 | 59 | 0.4 | 36 | 200 | 0 |  | 200 | 40
|  | 38 | 16174 |  | 1272.9 | 40 x 3,7 | 2.76 | 0.42 | 78 | 0.4 | 47 | 262 | 0 |  | 262 | 40
|  | 36 | 18485 |  | 1454.8 | 40 x 3,7 | 2.76 | 0.48 | 98 | 0.4 | 59 | 331 | 0 |  | 331 | 40
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -151
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-13
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 42 -

## Heating_cooling circuits-3
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 28 | 2311 |  | 181.9 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.9 | 242 | 250 | 0 |  | 250 | 25
| Heating/cooling floor | Tennis court-1-13 | 1990 |  | 181.9 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5787
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 50_A | 2311 |  | 181.9 | 25 x 2,3 | 0.35 | 0.15 | 24 | 0 | 0 | 8 | 0 |  | 8 | 25
|  | 50 | 2311 |  | 181.9 | 25 x 2,3 | 2.81 | 0.15 | 24 | 4.3 | 101 | 168 | 0 |  | 168 | 25
|  | 48 | 4621 |  | 363.7 | 25 x 2,3 | 2.76 | 0.31 | 80 | 1.9 | 79 | 301 | 0 |  | 301 | 25
|  | 46 | 6932 |  | 545.6 | 32 x 2,9 | 2.76 | 0.28 | 50 | 1.9 | 118 | 256 | 0 |  | 256 | 40
|  | 44 | 9243 |  | 727.4 | 32 x 2,9 | 2.76 | 0.37 | 82 | 1.9 | 189 | 416 | 0 |  | 416 | 40
|  | 42 | 11553 |  | 909.2 | 32 x 2,9 | 2.76 | 0.47 | 122 | 1.4 | 136 | 473 | 0 |  | 473 | 40
|  | 40 | 13864 |  | 1091.1 | 40 x 3,7 | 2.76 | 0.36 | 59 | 0.4 | 36 | 200 | 0 |  | 200 | 40
|  | 38 | 16174 |  | 1272.9 | 40 x 3,7 | 2.76 | 0.42 | 78 | 0.4 | 47 | 262 | 0 |  | 262 | 40
|  | 36 | 18485 |  | 1454.8 | 40 x 3,7 | 2.76 | 0.48 | 98 | 0.4 | 59 | 331 | 0 |  | 331 | 40
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -180
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-10
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 34 | 2310 |  | 181.8 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.6 | 162 | 171 | 0 |  | 171 | 25
| Heating/cooling floor | Tennis court-1-10 | 1989 |  | 181.8 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5781
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 45 | 2310 |  | 181.8 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.1 | 118 | 130 | 0 |  | 130 | 25
|  | 44 | 9243 |  | 727.4 | 32 x 2,9 | 2.76 | 0.37 | 82 | 1.9 | 189 | 416 | 0 |  | 416 | 40
|  | 42 | 11553 |  | 909.2 | 32 x 2,9 | 2.76 | 0.47 | 122 | 1.4 | 136 | 473 | 0 |  | 473 | 40
|  | 40 | 13864 |  | 1091.1 | 40 x 3,7 | 2.76 | 0.36 | 59 | 0.4 | 36 | 200 | 0 |  | 200 | 40
|  | 38 | 16174 |  | 1272.9 | 40 x 3,7 | 2.76 | 0.42 | 78 | 0.4 | 47 | 262 | 0 |  | 262 | 40
|  | 36 | 18485 |  | 1454.8 | 40 x 3,7 | 2.76 | 0.48 | 98 | 0.4 | 59 | 331 | 0 |  | 331 | 40
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 43 -

## Heating_cooling circuits-4
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -219
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-3
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 37 | 18487 |  | 1454.9 | 40 x 3,7 | 2.76 | 0.49 | 93 | 0.4 | 60 | 316 | 0 |  | 316 | 40
|  | 39 | 16176 |  | 1273 | 40 x 3,7 | 2.76 | 0.43 | 74 | 0.4 | 47 | 250 | 0 |  | 250 | 40
|  | 41 | 13865 |  | 1091.2 | 40 x 3,7 | 2.76 | 0.36 | 56 | 0.4 | 36 | 191 | 0 |  | 191 | 40
|  | 43 | 11555 |  | 909.4 | 32 x 2,9 | 2.76 | 0.47 | 115 | 1.4 | 137 | 455 | 0 |  | 455 | 40
|  | 45 | 9244 |  | 727.5 | 32 x 2,9 | 2.76 | 0.38 | 78 | 1.9 | 190 | 404 | 0 |  | 404 | 40
|  | 47 | 6933 |  | 545.6 | 32 x 2,9 | 2.76 | 0.28 | 47 | 1.9 | 119 | 248 | 0 |  | 248 | 40
|  | 48 | 2311 |  | 181.9 | 25 x 2,3 | 0.38 | 0.16 | 23 | 4.5 | 131 | 139 | 0 |  | 139 | 25
| Heating/cooling floor | Tennis court-1-3 | 1990 |  | 181.9 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5785
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 31 | 2311 |  | 181.9 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.9 | 180 | 192 | 0 |  | 192 | 25
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -250
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-7
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 37 | 18487 |  | 1454.9 | 40 x 3,7 | 2.76 | 0.49 | 93 | 0.4 | 60 | 316 | 0 |  | 316 | 40
|  | 39 | 16176 |  | 1273 | 40 x 3,7 | 2.76 | 0.43 | 74 | 0.4 | 47 | 250 | 0 |  | 250 | 40
|  | 40 | 2310 |  | 181.8 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.6 | 191 | 200 | 0 |  | 200 | 25
| Heating/cooling floor | Tennis court-1-7 | 1989 |  | 181.8 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5782
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 39 | 2310 |  | 181.8 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.6 | 190 | 202 | 0 |  | 202 | 25
|  | 38 | 16174 |  | 1272.9 | 40 x 3,7 | 2.76 | 0.42 | 78 | 0.4 | 47 | 262 | 0 |  | 262 | 40
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 44 -

## Heating_cooling circuits-5
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 36 | 18485 |  | 1454.8 | 40 x 3,7 | 2.76 | 0.48 | 98 | 0.4 | 59 | 331 | 0 |  | 331 | 40
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -293
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-4
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 37 | 18487 |  | 1454.9 | 40 x 3,7 | 2.76 | 0.49 | 93 | 0.4 | 60 | 316 | 0 |  | 316 | 40
|  | 39 | 16176 |  | 1273 | 40 x 3,7 | 2.76 | 0.43 | 74 | 0.4 | 47 | 250 | 0 |  | 250 | 40
|  | 41 | 13865 |  | 1091.2 | 40 x 3,7 | 2.76 | 0.36 | 56 | 0.4 | 36 | 191 | 0 |  | 191 | 40
|  | 43 | 11555 |  | 909.4 | 32 x 2,9 | 2.76 | 0.47 | 115 | 1.4 | 137 | 455 | 0 |  | 455 | 40
|  | 45 | 9244 |  | 727.5 | 32 x 2,9 | 2.76 | 0.38 | 78 | 1.9 | 190 | 404 | 0 |  | 404 | 40
|  | 46 | 2311 |  | 181.9 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.1 | 119 | 127 | 0 |  | 127 | 25
| Heating/cooling floor | Tennis court-1-4 | 1990 |  | 181.9 | 25x2.3 | 248.8 | 0.15 |  |  |  |  | 0 |  | 5788
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 33 | 2311 |  | 181.9 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.6 | 161 | 173 | 0 |  | 173 | 25
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -295
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-8
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 37 | 18487 |  | 1454.9 | 40 x 3,7 | 2.76 | 0.49 | 93 | 0.4 | 60 | 316 | 0 |  | 316 | 40
|  | 38 | 2311 |  | 181.9 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.6 | 243 | 252 | 0 |  | 252 | 25
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 45 -

## Heating_cooling circuits-6
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Heating/cooling floor | Tennis court-1-8 | 1990 |  | 181.9 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5786
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 41 | 2311 |  | 181.9 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.6 | 145 | 157 | 0 |  | 157 | 25
|  | 40 | 13864 |  | 1091.1 | 40 x 3,7 | 2.76 | 0.36 | 59 | 0.4 | 36 | 200 | 0 |  | 200 | 40
|  | 38 | 16174 |  | 1272.9 | 40 x 3,7 | 2.76 | 0.42 | 78 | 0.4 | 47 | 262 | 0 |  | 262 | 40
|  | 36 | 18485 |  | 1454.8 | 40 x 3,7 | 2.76 | 0.48 | 98 | 0.4 | 59 | 331 | 0 |  | 331 | 40
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -332
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-6
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 37 | 18487 |  | 1454.9 | 40 x 3,7 | 2.76 | 0.49 | 93 | 0.4 | 60 | 316 | 0 |  | 316 | 40
|  | 39 | 16176 |  | 1273 | 40 x 3,7 | 2.76 | 0.43 | 74 | 0.4 | 47 | 250 | 0 |  | 250 | 40
|  | 41 | 13865 |  | 1091.2 | 40 x 3,7 | 2.76 | 0.36 | 56 | 0.4 | 36 | 191 | 0 |  | 191 | 40
|  | 42 | 2311 |  | 181.8 | 25 x 2,3 | 0.38 | 0.16 | 23 | 3.6 | 146 | 154 | 0 |  | 154 | 25
| Heating/cooling floor | Tennis court-1-6 | 1989 |  | 181.8 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5783
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 37 | 2311 |  | 181.8 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.6 | 242 | 254 | 0 |  | 254 | 25
|  | 36 | 18485 |  | 1454.8 | 40 x 3,7 | 2.76 | 0.48 | 98 | 0.4 | 59 | 331 | 0 |  | 331 | 40
|  | 34 | 20795 |  | 1636.6 | 40 x 3,7 | 2.76 | 0.54 | 121 | 0.4 | 30 | 364 | 0 |  | 364 | 40
|  | 32 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 30 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.42 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 28 | 27729 |  | 2182.2 | 50 x 4,6 | 2.76 | 0.46 | 69 | 3.6 | 439 | 630 | 0 |  | 630 | 50
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -356
Circuit through Heating/cooling floor: |  |  |  | Tennis court-1-1
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 46 -

## Heating_cooling circuits-7
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 37.12 | 0.5 | 75 | 4.8 | 563 | 3354 | 0 |  | 3354 | 50
|  | 29 | 27728 |  | 2182.2 | 50 x 4,6 | 2.74 | 0.47 | 65 | 0.4 | 51 | 230 | 0 |  | 230 | 50
|  | 31 | 25418 |  | 2000.4 | 50 x 4,6 | 2.76 | 0.43 | 56 | 0.4 | 43 | 198 | 0 |  | 198 | 50
|  | 33 | 23107 |  | 1818.5 | 50 x 4,6 | 2.76 | 0.39 | 47 | 1.2 | 92 | 223 | 0 |  | 223 | 50
|  | 35 | 20797 |  | 1636.7 | 40 x 3,7 | 2.76 | 0.55 | 114 | 0.4 | 30 | 346 | 0 |  | 346 | 40
|  | 37 | 18487 |  | 1454.9 | 40 x 3,7 | 2.76 | 0.49 | 93 | 0.4 | 60 | 316 | 0 |  | 316 | 40
|  | 39 | 16176 |  | 1273 | 40 x 3,7 | 2.76 | 0.43 | 74 | 0.4 | 47 | 250 | 0 |  | 250 | 40
|  | 41 | 13865 |  | 1091.2 | 40 x 3,7 | 2.76 | 0.36 | 56 | 0.4 | 36 | 191 | 0 |  | 191 | 40
|  | 43 | 11555 |  | 909.4 | 32 x 2,9 | 2.76 | 0.47 | 115 | 1.4 | 137 | 455 | 0 |  | 455 | 40
|  | 45 | 9244 |  | 727.5 | 32 x 2,9 | 2.76 | 0.38 | 78 | 1.9 | 190 | 404 | 0 |  | 404 | 40
|  | 47 | 6933 |  | 545.6 | 32 x 2,9 | 2.76 | 0.28 | 47 | 1.9 | 119 | 248 | 0 |  | 248 | 40
|  | 49 | 4622 |  | 363.7 | 25 x 2,3 | 2.76 | 0.31 | 76 | 1.9 | 80 | 289 | 0 |  | 289 | 25
|  | 51 | 2311 |  | 181.9 | 25 x 2,3 | 2.83 | 0.16 | 23 | 4.3 | 101 | 165 | 0 |  | 165 | 25
|  | 51_A | 2311 |  | 181.9 | 25 x 2,3 | 0.24 | 0.16 | 23 | 0 | 0 | 5 | 0 |  | 5 | 25
| Heating/cooling floor | Tennis court-1-1 | 1990 |  | 181.9 | 25x2.3 | 248.7 | 0.15 |  |  |  |  | 0 |  | 5785
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 51 | 2311 |  | 181.9 | 25 x 2,3 | 0.49 | 0.15 | 24 | 3.6 | 203 | 215 | 0 |  | 215 | 25
|  | 27_A | 30039 |  | 2364.1 | 50 x 4,6 | 36.37 | 0.5 | 80 | 4.6 | 580 | 3472 | 0 |  | 3472 | 50
|  | 27 | 30039 |  | 2364.1 | 50 x 4,6 | 36.51 | 0.5 | 80 | 2.9 | 321 | 3223 | 0 |  | 3223 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -743
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-1
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.49 | 93 | 0.4 | 60 | 318 | 0 |  | 318 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.43 | 74 | 0.4 | 47 | 251 | 0 |  | 251 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.37 | 56 | 0.4 | 36 | 192 | 0 |  | 192 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 115 | 1.4 | 137 | 456 | 0 |  | 456 | 40
|  | 20 | 9257 |  | 728.5 | 32 x 2,9 | 2.77 | 0.38 | 78 | 1.9 | 190 | 406 | 0 |  | 406 | 40
|  | 22 | 6943 |  | 546.4 | 32 x 2,9 | 2.77 | 0.28 | 47 | 1.9 | 119 | 249 | 0 |  | 249 | 40
|  | 24 | 4628 |  | 364.3 | 25 x 2,3 | 2.77 | 0.31 | 76 | 1.9 | 80 | 290 | 0 |  | 290 | 25
|  | 26 | 2314 |  | 182.1 | 25 x 2,3 | 2.84 | 0.16 | 23 | 4.3 | 102 | 166 | 0 |  | 166 | 25
|  | 26_A | 2314 |  | 182.1 | 25 x 2,3 | 0.25 | 0.16 | 23 | 0 | 0 | 6 | 0 |  | 6 | 25
| Heating/cooling floor | Tennis court-2-1 | 1993 |  | 182.1 | 25x2.3 | 249.1 | 0.15 |  |  |  |  | 0 |  | 5808
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 26_A | 2314 |  | 182.1 | 25 x 2,3 | 0.15 | 0.15 | 24 | 0 | 0 | 4 | 0 |  | 4 | 25
|  | 26 | 2314 |  | 182.1 | 25 x 2,3 | 2.84 | 0.15 | 24 | 4.3 | 101 | 169 | 0 |  | 169 | 25
|  | 24 | 4628 |  | 364.3 | 25 x 2,3 | 2.77 | 0.31 | 81 | 1.9 | 79 | 303 | 0 |  | 303 | 25
|  | 22 | 6943 |  | 546.4 | 32 x 2,9 | 2.77 | 0.28 | 50 | 1.9 | 118 | 257 | 0 |  | 257 | 40
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 47 -

## Heating_cooling circuits-8
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 20 | 9257 |  | 728.5 | 32 x 2,9 | 2.77 | 0.38 | 83 | 1.9 | 189 | 418 | 0 |  | 418 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 122 | 1.4 | 136 | 475 | 0 |  | 475 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.36 | 60 | 0.4 | 36 | 201 | 0 |  | 201 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.42 | 78 | 0.4 | 47 | 263 | 0 |  | 263 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.48 | 99 | 0.4 | 59 | 332 | 0 |  | 332 | 40
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -6470
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-2
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.49 | 93 | 0.4 | 60 | 318 | 0 |  | 318 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.43 | 74 | 0.4 | 47 | 251 | 0 |  | 251 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.37 | 56 | 0.4 | 36 | 192 | 0 |  | 192 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 115 | 1.4 | 137 | 456 | 0 |  | 456 | 40
|  | 20 | 9257 |  | 728.5 | 32 x 2,9 | 2.77 | 0.38 | 78 | 1.9 | 190 | 406 | 0 |  | 406 | 40
|  | 22 | 6943 |  | 546.4 | 32 x 2,9 | 2.77 | 0.28 | 47 | 1.9 | 119 | 249 | 0 |  | 249 | 40
|  | 24 | 4628 |  | 364.3 | 25 x 2,3 | 2.77 | 0.31 | 76 | 1.9 | 80 | 290 | 0 |  | 290 | 25
|  | 25 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 4.5 | 155 | 163 | 0 |  | 163 | 25
| Heating/cooling floor | Tennis court-2-2 | 1993 |  | 182.1 | 25x2.3 | 249.1 | 0.15 |  |  |  |  | 0 |  | 5809
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 25 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 4.5 | 154 | 161 | 0 |  | 161 | 25
|  | 24 | 4628 |  | 364.3 | 25 x 2,3 | 2.77 | 0.31 | 81 | 1.9 | 79 | 303 | 0 |  | 303 | 25
|  | 22 | 6943 |  | 546.4 | 32 x 2,9 | 2.77 | 0.28 | 50 | 1.9 | 118 | 257 | 0 |  | 257 | 40
|  | 20 | 9257 |  | 728.5 | 32 x 2,9 | 2.77 | 0.38 | 83 | 1.9 | 189 | 418 | 0 |  | 418 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 122 | 1.4 | 136 | 475 | 0 |  | 475 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.36 | 60 | 0.4 | 36 | 201 | 0 |  | 201 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.42 | 78 | 0.4 | 47 | 263 | 0 |  | 263 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.48 | 99 | 0.4 | 59 | 332 | 0 |  | 332 | 40
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -6489
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 48 -

## Heating_cooling circuits-9
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-3
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.49 | 93 | 0.4 | 60 | 318 | 0 |  | 318 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.43 | 74 | 0.4 | 47 | 251 | 0 |  | 251 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.37 | 56 | 0.4 | 36 | 192 | 0 |  | 192 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 115 | 1.4 | 137 | 456 | 0 |  | 456 | 40
|  | 20 | 9257 |  | 728.5 | 32 x 2,9 | 2.77 | 0.38 | 78 | 1.9 | 190 | 406 | 0 |  | 406 | 40
|  | 22 | 6943 |  | 546.4 | 32 x 2,9 | 2.77 | 0.28 | 47 | 1.9 | 119 | 249 | 0 |  | 249 | 40
|  | 23 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 4.5 | 131 | 140 | 0 |  | 140 | 25
| Heating/cooling floor | Tennis court-2-3 | 1992 |  | 182.1 | 25x2.3 | 249.1 | 0.15 |  |  |  |  | 0 |  | 5807
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 23 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 4.5 | 131 | 138 | 0 |  | 138 | 25
|  | 22 | 6943 |  | 546.4 | 32 x 2,9 | 2.77 | 0.28 | 50 | 1.9 | 118 | 257 | 0 |  | 257 | 40
|  | 20 | 9257 |  | 728.5 | 32 x 2,9 | 2.77 | 0.38 | 83 | 1.9 | 189 | 418 | 0 |  | 418 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 122 | 1.4 | 136 | 475 | 0 |  | 475 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.36 | 60 | 0.4 | 36 | 201 | 0 |  | 201 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.42 | 78 | 0.4 | 47 | 263 | 0 |  | 263 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.48 | 99 | 0.4 | 59 | 332 | 0 |  | 332 | 40
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -7130
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-4
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.49 | 93 | 0.4 | 60 | 318 | 0 |  | 318 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.43 | 74 | 0.4 | 47 | 251 | 0 |  | 251 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.37 | 56 | 0.4 | 36 | 192 | 0 |  | 192 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 115 | 1.4 | 137 | 456 | 0 |  | 456 | 40
|  | 20 | 9257 |  | 728.5 | 32 x 2,9 | 2.77 | 0.38 | 78 | 1.9 | 190 | 406 | 0 |  | 406 | 40
|  | 21 | 2315 |  | 182.2 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.1 | 119 | 128 | 0 |  | 128 | 25
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 49 -

## Heating_cooling circuits-10
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Heating/cooling floor | Tennis court-2-4 | 1993 |  | 182.2 | 25x2.3 | 249.1 | 0.15 |  |  |  |  | 0 |  | 5811
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 21 | 2315 |  | 182.2 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.1 | 118 | 126 | 0 |  | 126 | 25
|  | 20 | 9257 |  | 728.5 | 32 x 2,9 | 2.77 | 0.38 | 83 | 1.9 | 189 | 418 | 0 |  | 418 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 122 | 1.4 | 136 | 475 | 0 |  | 475 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.36 | 60 | 0.4 | 36 | 201 | 0 |  | 201 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.42 | 78 | 0.4 | 47 | 263 | 0 |  | 263 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.48 | 99 | 0.4 | 59 | 332 | 0 |  | 332 | 40
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -7656
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-5
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.49 | 93 | 0.4 | 60 | 318 | 0 |  | 318 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.43 | 74 | 0.4 | 47 | 251 | 0 |  | 251 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.37 | 56 | 0.4 | 36 | 192 | 0 |  | 192 | 40
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 115 | 1.4 | 137 | 456 | 0 |  | 456 | 40
|  | 19 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.1 | 175 | 183 | 0 |  | 183 | 25
| Heating/cooling floor | Tennis court-2-5 | 1992 |  | 182.1 | 25x2.3 | 249 | 0.15 |  |  |  |  | 0 |  | 5806
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 19 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.1 | 174 | 181 | 0 |  | 181 | 25
|  | 18 | 11571 |  | 910.6 | 32 x 2,9 | 2.77 | 0.47 | 122 | 1.4 | 136 | 475 | 0 |  | 475 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.36 | 60 | 0.4 | 36 | 201 | 0 |  | 201 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.42 | 78 | 0.4 | 47 | 263 | 0 |  | 263 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.48 | 99 | 0.4 | 59 | 332 | 0 |  | 332 | 40
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -8374
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 50 -

## Heating_cooling circuits-11
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-6
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.49 | 93 | 0.4 | 60 | 318 | 0 |  | 318 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.43 | 74 | 0.4 | 47 | 251 | 0 |  | 251 | 40
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.37 | 56 | 0.4 | 36 | 192 | 0 |  | 192 | 40
|  | 17 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.6 | 146 | 155 | 0 |  | 155 | 25
| Heating/cooling floor | Tennis court-2-6 | 1992 |  | 182.1 | 25x2.3 | 249 | 0.15 |  |  |  |  | 0 |  | 5805
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 17 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.6 | 145 | 152 | 0 |  | 152 | 25
|  | 16 | 13885 |  | 1092.7 | 40 x 3,7 | 2.77 | 0.36 | 60 | 0.4 | 36 | 201 | 0 |  | 201 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.42 | 78 | 0.4 | 47 | 263 | 0 |  | 263 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.48 | 99 | 0.4 | 59 | 332 | 0 |  | 332 | 40
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -9362
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-7
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.49 | 93 | 0.4 | 60 | 318 | 0 |  | 318 | 40
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.43 | 74 | 0.4 | 47 | 251 | 0 |  | 251 | 40
|  | 15 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.6 | 191 | 200 | 0 |  | 200 | 25
| Heating/cooling floor | Tennis court-2-7 | 1992 |  | 182.1 | 25x2.3 | 249 | 0.15 |  |  |  |  | 0 |  | 5805
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 15 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.6 | 191 | 198 | 0 |  | 198 | 25
|  | 14 | 16198 |  | 1274.8 | 40 x 3,7 | 2.77 | 0.42 | 78 | 0.4 | 47 | 263 | 0 |  | 263 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.48 | 99 | 0.4 | 59 | 332 | 0 |  | 332 | 40
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 51 -

## Heating_cooling circuits-12
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -9664
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-8
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.49 | 93 | 0.4 | 60 | 318 | 0 |  | 318 | 40
|  | 13 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.6 | 244 | 253 | 0 |  | 253 | 25
| Heating/cooling floor | Tennis court-2-8 | 1993 |  | 182.1 | 25x2.3 | 249.1 | 0.15 |  |  |  |  | 0 |  | 5808
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 13 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.6 | 243 | 250 | 0 |  | 250 | 25
|  | 12 | 18513 |  | 1457 | 40 x 3,7 | 2.77 | 0.48 | 99 | 0.4 | 59 | 332 | 0 |  | 332 | 40
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -10069
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-9
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 115 | 0.4 | 30 | 347 | 0 |  | 347 | 40
|  | 11 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.6 | 304 | 312 | 0 |  | 312 | 25
| Heating/cooling floor | Tennis court-2-9 | 1992 |  | 182.1 | 25x2.3 | 249 | 0.15 |  |  |  |  | 0 |  | 5804
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 11 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.6 | 302 | 309 | 0 |  | 309 | 25
|  | 10 | 20826 |  | 1639 | 40 x 3,7 | 2.77 | 0.55 | 121 | 0.4 | 30 | 366 | 0 |  | 366 | 40
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 52 -

## Heating_cooling circuits-13
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -10605
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-10
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 47 | 1.2 | 93 | 224 | 0 |  | 224 | 50
|  | 9 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.6 | 163 | 171 | 0 |  | 171 | 25
| Heating/cooling floor | Tennis court-2-10 | 1992 |  | 182.1 | 25x2.3 | 249 | 0.15 |  |  |  |  | 0 |  | 5804
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 9 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.6 | 162 | 169 | 0 |  | 169 | 25
|  | 8 | 23140 |  | 1821.1 | 50 x 4,6 | 2.77 | 0.39 | 50 | 1.2 | 92 | 231 | 0 |  | 231 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -11600
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-11
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 56 | 0.4 | 43 | 199 | 0 |  | 199 | 50
|  | 7 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.9 | 181 | 190 | 0 |  | 190 | 25
| Heating/cooling floor | Tennis court-2-11 | 1993 |  | 182.1 | 25x2.3 | 249.1 | 0.15 |  |  |  |  | 0 |  | 5808
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 7 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.9 | 180 | 187 | 0 |  | 187 | 25
|  | 6 | 25454 |  | 2003.2 | 50 x 4,6 | 2.77 | 0.43 | 59 | 0.4 | 43 | 207 | 0 |  | 207 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -12014
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-12
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 53 -

## Heating_cooling circuits-14
Project: Tichelmann Installation System
Label |  | Symbol | ΦH |  | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W |  | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.47 | 65 | 0.4 | 51 | 233 | 0 |  | 233 | 50
|  | 5 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.9 | 210 | 219 | 0 |  | 219 | 25
| Heating/cooling floor | Tennis court-2-12 | 1992 |  | 182.1 | 25x2.3 | 249 | 0.15 |  |  |  |  | 0 |  | 5803
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 5 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.9 | 210 | 217 | 0 |  | 217 | 25
|  | 4 | 27768 |  | 2185.3 | 50 x 4,6 | 2.79 | 0.46 | 69 | 0.4 | 51 | 244 | 0 |  | 244 | 50
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -12366
Circuit through Heating/cooling floor: |  |  |  | Tennis court-2-13
| Source | 1 | 60551 |  | 4731.6 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -23297
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 21.12 | 0.45 | 37 | 8.3 | 816 | 1588 | 0 |  | 1588 | 70
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 0.53 | 0.5 | 75 | 3.6 | 378 | 418 | 0 |  | 418 | 50
|  | 3 | 2314 |  | 182.1 | 25 x 2,3 | 0.39 | 0.16 | 23 | 3.9 | 242 | 251 | 0 |  | 251 | 25
| Heating/cooling floor | Tennis court-2-13 | 1993 |  | 182.1 | 25x2.3 | 249.1 | 0.15 |  |  |  |  | 0 |  | 5809
| Heating/cooling floor (Thermosiphon) | [13 empty] | 22
|  | 3 | 2314 |  | 182.1 | 25 x 2,3 | 0.3 | 0.15 | 24 | 3.9 | 241 | 248 | 0 |  | 248 | 25
|  | 2 | 30082 |  | 2367.5 | 50 x 4,6 | 2.96 | 0.5 | 80 | 3.6 | 377 | 613 | 0 |  | 613 | 50
|  | 1 | 60121 |  | 4731.6 | 75 x 6,8 | 19.72 | 0.44 | 39 | 8.3 | 813 | 1574 | 0 |  | 1574 | 70
[13 empty] | Total: |  | -12773
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 54 -

## Room charts
Project: Tichelmann Installation System
Room chart: Tennis court
Storey: | 0
Building unit: | 01
Manifolds in room: | -
Automatic control components: | -
Heating/cooling floor, Structure: 1,720 / 0,129999999999999
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  | - 55 -

## Room charts-1
Project: Tichelmann Installation System
Heating/cooling zone symbol |  | Occupied / peripheral zone | Area | Pipe spacing | Pipe type |  |  |  |  | Type of heating-cooling surface |  | Pipe arrangement | Overall circuit length (feeds + loop) |  | Manifold outlet number
Symbol<br/>Covering Rλ,B |  | Type | A | VA | Pipe |  |  |  |  | Type |  | Pipe laying pattern | Ltot |  | Outlet no.
(m²·K)/W |  |  | m² | mm | [8 empty] | m
Areas supplied with no manifold. Source: 1 | [5 empty] | , | Storey: | 0, | Bld. unit: |  | 01
| Tennis court-1-1 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 10 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-2 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 8 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-3 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 10 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-4 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 7 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.8
| Tennis court-1-5 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 11 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-6 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 11 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-7 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 12 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-8 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 9 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-9 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 12 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-10 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 13 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-11 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 9 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-12 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 13 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-1-13 | OZ | 49.7 | 200 | PEX pipe 25x2.3 Coil 8 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 248.7
| Tennis court-2-1 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 3 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249.1
| Tennis court-2-2 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 2 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249.1
| Tennis court-2-3 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 4 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249.1
| Tennis court-2-4 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 1 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249.1
| Tennis court-2-5 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 4 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249
| Tennis court-2-6 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 5 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249
| Tennis court-2-7 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 5 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249
| Tennis court-2-8 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 2 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249.1
| Tennis court-2-9 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 6 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249
| Tennis court-2-10 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 6 |  |  |  |  | Heating/cooling floor |  | Spiral pipe pattern | 249
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 56 -

## Room charts-2
Project: Tichelmann Installation System
Heating/cooling zone symbol |  | Occupied / peripheral zone | Area | Pipe spacing | Pipe type | Type of heating-cooling surface | Pipe arrangement | Overall circuit length (feeds + loop) |  | Manifold outlet number
Symbol<br/>Covering Rλ,B |  | Type | A | VA | Pipe | Type | Pipe laying pattern | Ltot |  | Outlet no.
(m²·K)/W |  |  | m² | mm |  |  |  | m
| Tennis court-2-11 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 3 | Heating/cooling floor | Spiral pipe pattern | 249.1
| Tennis court-2-12 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 7 | Heating/cooling floor | Spiral pipe pattern | 249
| Tennis court-2-13 | OZ | 49.8 | 200 | PEX pipe 25x2.3 Coil 1 | Heating/cooling floor | Spiral pipe pattern | 249.1
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [8 empty] | - 57 -

## Radiant system installation
Project: Tichelmann Installation System
Radiant system installation parameters
Heating/cooling zone symbol and thermal resistance of covering |  | Occupied / peripheral zone | Area | Pipe spacing |  | Pipe type Coil Manner of arrangement Number of circuits |  |  |  |  | Overall circuit length (feeds + loop) | Valve setting | Heating/cooling surface structure
Symbol<br/>Covering Rλ,B |  | Type | A | VA |  | Pipe |  |  |  |  | Ltot | Valve set. | Structure
(m²·K)/W |  |  | m² | mm | [6 empty] | m
Areas supplied with no manifold. Source: 1 |  |  |  |  | , |  | Storey: | 0, | Bld. unit: | 01
Room: Tennis court, No. of HZs: 26 / 26, Pipe laying system: Floor clip rail system
| Tennis court-1-1 | OZ | 49.7 | 200 |  | PEX pipe 25x2.3 Coil 10 Spiral pipe pattern |  |  |  |  | 248.7 |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-2 | OZ | 49.7 | 200 |  | PEX pipe 25x2.3 Coil 8 Spiral pipe pattern |  |  |  |  | 248.7 |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-3 | OZ | 49.7 | 200 |  | PEX pipe 25x2.3 Coil 10 Spiral pipe pattern |  |  |  |  | 248.7 |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-4 | OZ | 49.8 | 200 |  | PEX pipe 25x2.3 Coil 7 Spiral pipe pattern |  |  |  |  | 248.8 |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-5 | OZ | 49.7 | 200 |  | PEX pipe 25x2.3 Coil 11 Spiral pipe pattern |  |  |  |  | 248.7 |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [13 empty] | - 58 -

## Radiant system installation-1
Project: Tichelmann Installation System
Symbol<br/>Covering Rλ,B |  |  | Type |  | A |  | VA |  | Pipe |  | Ltot |  | Valve set. | Structure
(m²·K)/W |  |  |  |  | m² |  | mm |  |  |  | m
| Tennis court-1-6 | OZ |  | 49.7 |  | 200 |  | PEX pipe 25x2.3 Coil 11 Spiral pipe pattern |  | 248.7 |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-7 |  | OZ |  | 49.7 |  | 200 |  | PEX pipe 25x2.3 Coil 12 Spiral pipe pattern |  | 248.7 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-8 |  | OZ |  | 49.7 |  | 200 |  | PEX pipe 25x2.3 Coil 9 Spiral pipe pattern |  | 248.7 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-9 |  | OZ |  | 49.7 |  | 200 |  | PEX pipe 25x2.3 Coil 12 Spiral pipe pattern |  | 248.7 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-10 |  | OZ |  | 49.7 |  | 200 |  | PEX pipe 25x2.3 Coil 13 Spiral pipe pattern |  | 248.7 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-11 |  | OZ |  | 49.7 |  | 200 |  | PEX pipe 25x2.3 Coil 9 Spiral pipe pattern |  | 248.7 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-12 |  | OZ |  | 49.7 |  | 200 |  | PEX pipe 25x2.3 Coil 13 Spiral pipe pattern |  | 248.7 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-1-13 |  | OZ |  | 49.7 |  | 200 |  | PEX pipe 25x2.3 Coil 8 Spiral pipe pattern |  | 248.7 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-1 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 3 Spiral pipe pattern |  | 249.1 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [14 empty] | - 59 -

## Radiant system installation-2
Project: Tichelmann Installation System
Symbol<br/>Covering Rλ,B |  |  | Type |  | A |  | VA |  | Pipe |  | Ltot |  | Valve set. | Structure
(m²·K)/W |  |  |  |  | m² |  | mm |  |  |  | m
| Tennis court-2-2 | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 2 Spiral pipe pattern |  | 249.1 |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-3 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 4 Spiral pipe pattern |  | 249.1 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-4 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 1 Spiral pipe pattern |  | 249.1 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-5 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 4 Spiral pipe pattern |  | 249 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-6 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 5 Spiral pipe pattern |  | 249 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-7 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 5 Spiral pipe pattern |  | 249 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-8 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 2 Spiral pipe pattern |  | 249.1 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-9 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 6 Spiral pipe pattern |  | 249 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-10 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 6 Spiral pipe pattern |  | 249 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [14 empty] | - 60 -

## Radiant system installation-3
Project: Tichelmann Installation System
Symbol<br/>Covering Rλ,B |  |  | Type |  | A |  | VA |  | Pipe |  | Ltot |  | Valve set. | Structure
(m²·K)/W |  |  |  |  | m² |  | mm |  |  |  | m
| Tennis court-2-11 | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 3 Spiral pipe pattern |  | 249.1 |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-12 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 7 Spiral pipe pattern |  | 249 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
| Tennis court-2-13 |  | OZ |  | 49.8 |  | 200 |  | PEX pipe 25x2.3 Coil 1 Spiral pipe pattern |  | 249.1 |  |  | Screed 7,4 cm (Su 4,5 cm) Styrofoam insulation board (lambda 0,04) 20 mm Hydroinsulation PE Foil 0.2 mm Rλ,floor = 0,300 (m²·K)/W
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [14 empty] | - 61 -

## Coils allocation
Project: Tichelmann Installation System
Coils allocation
Coils |  |  | Total coil length | H/C Area length | Remaining
|  |  | m | m | m
Coil 1 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 498.22 | 101.78
| Symbol | H/C Area length [m]
| Tennis court-2-13 | 249.1
| Tennis court-2-4 | 249.1
Coil 2 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 498.17 | 101.83
| Symbol | H/C Area length [m]
| Tennis court-2-2 | 249.1
| Tennis court-2-8 | 249.1
Coil 3 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 498.15 | 101.85
| Symbol | H/C Area length [m]
| Tennis court-2-1 | 249.1
| Tennis court-2-11 | 249.1
Coil 4 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 498.1 | 101.9
| Symbol | H/C Area length [m]
| Tennis court-2-3 | 249.1
| Tennis court-2-5 | 249
Coil 5 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 498.05 | 101.95
| Symbol | H/C Area length [m]
| Tennis court-2-6 | 249
| Tennis court-2-7 | 249
Coil 6 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 498.02 | 101.98
| Symbol | H/C Area length [m]
| Tennis court-2-10 | 249
| Tennis court-2-9 | 249
Coil 7 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 497.77 | 102.23
| Symbol | H/C Area length [m]
| Tennis court-2-12 | 249
| Tennis court-1-4 | 248.8
Coil 8 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 497.48 | 102.52
| Symbol | H/C Area length [m]
| Tennis court-1-13 | 248.7
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  |  |  |  | - 62 -

## Coils allocation-1
Project: Tichelmann Installation System
Coils |  |  | Total coil length | H/C Area length | Remaining
|  |  | m | m | m
| Symbol | H/C Area length [m]
| Tennis court-1-2 | 248.7
Coil 9 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 497.45 | 102.55
| Symbol | H/C Area length [m]
| Tennis court-1-11 | 248.7
| Tennis court-1-8 | 248.7
Coil 10 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 497.43 | 102.57
| Symbol | H/C Area length [m]
| Tennis court-1-1 | 248.7
| Tennis court-1-3 | 248.7
Coil 11 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 497.37 | 102.63
| Symbol | H/C Area length [m]
| Tennis court-1-5 | 248.7
| Tennis court-1-6 | 248.7
Coil 12 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 497.33 | 102.67
| Symbol | H/C Area length [m]
| Tennis court-1-7 | 248.7
| Tennis court-1-9 | 248.7
Coil 13 PEX pipe 25x2.3, Coil 600 m |  |  | 600 | 497.31 | 102.7
| Symbol | H/C Area length [m]
| Tennis court-1-10 | 248.7
| Tennis court-1-12 | 248.7
Summary |  |  | 7800 | 6470.85 | 1329.15
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  |  |  |  | - 63 -

## List of pipes, pipe fitting
Project: Tichelmann Installation System
List of pipes, pipe fittings and couplings
Product |  | Size | Catalogue code |  | Quantity | Unit
Brass and steel pipe couplings and fittings
Pipe fittings
| Female connector, reduction, imperial | 2½"FT - 2"FT |  |  | 4 | pcs.
| Tee | 1¼"FT - 1"FT - 1¼"FT |  |  | 8 | pcs.
PEX (pipes and fittings) acc. to EN ISO 15875
Pipes
| Pipe PN6 in coils | 25 x 2,3 |  |  | 43 | m
| Pipe PN6 in coils | 32 x 2,9 |  |  | 34 | m
| Pipe PN6 in coils | 40 x 3,7 |  |  | 45 | m
| Pipe PN6 in coils | 50 x 4,6 |  |  | 147 | m
| Pipe PN6 in coils | 75 x 6,8 |  |  | 41 | m
Pipe fittings
| Adapter PN6 | 25 - 1"MT |  |  | 68 | pcs.
| Adapter PN6 | 32 - 1"MT |  |  | 4 | pcs.
| Adapter PN6 | 32 - 1¼"MT |  |  | 20 | pcs.
| Adapter PN6 | 40 - 1¼"MT |  |  | 8 | pcs.
| Adapter PN6 | 50 - 1¼"MT |  |  | 16 | pcs.
| Adapter PN6 | 75 - 2½"MT |  |  | 20 | pcs.
| Bend support | 25 - 25 |  |  | 100 | pcs.
| Connection FT | 1¼"FT - 1¼"FT |  |  | 8 | pcs.
| Connection FT-MT | 1¼"MT - 1"FT |  |  | 11 | pcs.
| Connection FT-MT | 2"MT - 1"FT |  |  | 1 | pcs.
| Connection FT-MT | 2"MT - 1¼"FT |  |  | 6 | pcs.
| Elbow | 1"FT |  |  | 4 | pcs.
| Elbow | 1¼"FT |  |  | 3 | pcs.
| Elbow | 2½"FT |  |  | 8 | pcs.
| Reduction tee PN6 | 40 - 1"FT - 40 |  |  | 20 | pcs.
| Reduction tee PN6 | 50 - 1¼"FT - 50 |  |  | 11 | pcs.
| Tee | 1"FT - 1"FT - 1"FT |  |  | 8 | pcs.
| Tee | 2"FT - 2"FT - 2"FT |  |  | 1 | pcs.
| Tee FT | 75 - 2"FT - 75 |  |  | 2 | pcs.
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  |  |  | - 64 -

## List of pipes, pipe fitting-1
Project: Tichelmann Installation System
List of insulation
Product |  | Size | Catalogue code |  | Quantity | Unit
Standard insulation catalogue
Lagging
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=25 mm, Th=25 mm |  |  | 43 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=35 mm, Th=40 mm |  |  | 34 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=42 mm, Th=40 mm |  |  | 45 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=54 mm, Th=50 mm |  |  | 147 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=76 mm, Th=70 mm |  |  | 41 | m
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  |  |  | - 65 -

## List of pipes, pipe fitting-2
Project: Tichelmann Installation System
List of radiant heating components
Product |  | Size | Catalogue code |  | Quantity | Unit
Basic radiant systems
Coils
| PEX pipe | 25x2.3, Coil 600 m | any producer |  | 7800 | m
Structural slabs
| System plate | 30 mm | any producer |  | 1295 | m²
Insulation plates
| Hydroinsulation | PE Foil 0.2 mm | any producer |  | 1424 | m²
| Styrofoam insulation board (lambda 0,04) | 20 mm | any producer |  | 1295 | m²
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  |  |  | - 66 -

## List of pipes, pipe fitting-3
Project: Tichelmann Installation System
Product |  | Size | Catalogue code |  | Quantity | Unit
Accessories
| Clip rail |  | any producer |  | 1036 | m
| Edging strip |  | any producer |  | 144 | m
| Expansion joint profile |  | any producer |  | 36 | m
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 |  |  |  | - 67 -

## Pipes summary
Project: Tichelmann Installation System
Pipes summary
Product | Size | Catalogue code | Insulated | Non-insulated | User specified | Sized | Under design |  | Existing | From radiant systems
|  |  | m | m | m | m | m |  | m | m
PEX pipe | 25x2.3 | any producer | [7 empty] | 6470,85
Pipe PN6 in coils | 25 x 2,3 |  | 42,08 |  |  | 42,08 | 42,08
Pipe PN6 in coils | 32 x 2,9 |  | 33,19 |  |  | 33,19 | 33,19
Pipe PN6 in coils | 40 x 3,7 |  | 44,25 |  |  | 44,25 | 44,25
Pipe PN6 in coils | 50 x 4,6 |  | 146,71 |  |  | 146,71 | 146,71
Pipe PN6 in coils | 75 x 6,8 |  | 40,85 |  |  | 40,85 | 40,85
InstalSystem 5 EN (BETA) (Rev. 0.0.B30A1) © InstalSoft 1996-2016 | [7 empty] | - 68 -