## Front page
Project
Project number: | 1 | Project version:
Description: | Example of radiant heating installation with radiant ceiling steel panels
Street:
Postal code and city: |  | Telephone:
Country: |  | Fax:
WWW:
E-mail:
Comment
Project developer
Project subject: | InstalSoft s.c.
Street: | Moniuszki 8b
Postal code and city: | Chorzów | Telephone: | 48327505200
Country: | Poland | Fax:
WWW: | www.instalsoft.com
E-mail: | info@instalsoft.com.pl
VAT-id:
Comment
File info
File name: | C:\Users\misk\Documents\06-HS\SUZ-RHP-promienniki-v5\Installation-with-ceiling-systems-in-commercial-building-end.isproj
Program version: | 5.0 (Rev. 0.0.B33)
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 |  |  |  | - 1 -

## Components on pipe-runs
Project: Example of radiant heating installation with radiant ceiling steel panels
Components on pipe-runs
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 1, Source: 1, m= 1277,3 kg/h, Diameter: 35 x 1,5 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Flange PN16 F40 PN16 | DN40_16 |  |  |  | 0
| Copper pipes and fittings EN 1057 | Coupling MT 35 - 1½"MT |  | 0.1 |  |  | 10
| Copper pipes and fittings EN 1057 | Tee 35 - 28 - 22 |  |  |  |  | 0
| Copper pipes and fittings EN 1057 | Elbow 90° 35 - 35 |  | 1.6 |  |  | 157
| Copper pipes and fittings EN 1057 | Elbow 90° 35 - 35 |  | 1.6 |  |  | 157
Pipe-run (R) 1, Source: 1, m= 1277,3 kg/h, Diameter: 35 x 1,5 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 35 mm 40 mm
| Brass and steel pipe couplings and fittings | Flange PN16 F40 PN16 | DN40_16 |  |  |  | 0
| Copper pipes and fittings EN 1057 | Coupling MT 35 - 1½"MT |  | 0.1 |  |  | 10
| Copper pipes and fittings EN 1057 | Tee 28 - 35 - 22 |  |  |  |  | 0
| Copper pipes and fittings EN 1057 | Elbow 90° 35 - 35 |  | 1.6 |  |  | 157
Pipe-run (S) 10, Source: 1, m= 292,7 kg/h, Diameter: 18 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 18 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  | 0.7 |  |  | 53
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  |  |  |  | 0
Pipe-run (R) 10, Source: 1, m= 52,8 kg/h, Diameter: 12 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 12 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 28 - 12 - 28 |  | 2.1 |  |  | 162
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 1"FT - ½"FT |  | 0.4 |  |  | 7
| Brass and steel pipe couplings and fittings | Nipple, straight, imperial ½"MT - ½"MT |  | 0.4 |  |  | 7
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 21150
| Copper pipes and fittings EN 1057 | Coupling MT 12 - ½"MT |  | 0.4 |  |  | 7
Pipe-run (S) 11, Source: 1, m= 146,5 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  | 2.1 |  |  | 173
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 2 -

## Components on pipe-runs-1
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 13
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (R) 11, Source: 1, m= 638,5 kg/h, Diameter: 28 x 1,5 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 28 mm 40 mm
| Copper pipes and fittings EN 1057 | Tee 28 - 12 - 28 |  | 0.7 |  |  | 54
| Copper pipes and fittings EN 1057 | Tee 28 - 12 - 22 |  |  |  |  | 0
Pipe-run (S) 12, Source: 1, m= 146,3 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  | 0.9 |  |  | 74
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 13
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Bend 90° 15 - 15 |  | 1.7 |  |  | 80
Pipe-run (R) 12, Source: 1, m= 52,6 kg/h, Diameter: 12 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 12 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 28 - 12 - 22 |  | 2.1 |  |  | 138
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 1"FT - ½"FT |  | 0.4 |  |  | 7
| Brass and steel pipe couplings and fittings | Nipple, straight, imperial ½"MT - ½"MT |  | 0.4 |  |  | 7
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 20900
| Copper pipes and fittings EN 1057 | Coupling MT 12 - ½"MT |  | 0.4 |  |  | 7
Pipe-run (S) 13, Source: 1, m= 586,0 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 3 -

## Components on pipe-runs-2
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| Copper pipes and fittings EN 1057 | Tee 35 - 28 - 22 |  | 0.7 |  |  | 69
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  |  |  |  | 0
| Copper pipes and fittings EN 1057 | Bend 90° 22 - 22 |  | 1 |  |  | 136
| Copper pipes and fittings EN 1057 | Bend 90° 22 - 22 |  | 1 |  |  | 136
Pipe-run (R) 13, Source: 1, m= 586,0 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 28 - 12 - 22 |  | 0.7 |  |  | 46
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  |  |  |  | 0
| Copper pipes and fittings EN 1057 | Bend 90° 22 - 22 |  | 1 |  |  | 135
Pipe-run (S) 14, Source: 1, m= 146,7 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  | 2.1 |  |  | 285
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 29
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 13
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (R) 14, Source: 1, m= 146,7 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  | 2.1 |  |  | 284
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 18113
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (S) 15, Source: 1, m= 439,3 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 4 -

## Components on pipe-runs-3
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  | 0.7 |  |  | 95
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  |  |  |  | 0
Pipe-run (R) 15, Source: 1, m= 439,3 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  | 0.7 |  |  | 95
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  |  |  |  | 0
Pipe-run (S) 16, Source: 1, m= 146,6 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  | 2.1 |  |  | 160
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 29
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 13
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (R) 16, Source: 1, m= 146,6 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  | 2.1 |  |  | 160
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 17904
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (S) 17, Source: 1, m= 292,7 kg/h, Diameter: 18 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 18 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  | 0.7 |  |  | 53
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  |  |  |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 5 -

## Components on pipe-runs-4
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (R) 17, Source: 1, m= 292,7 kg/h, Diameter: 18 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 18 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  | 0.7 |  |  | 53
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  |  |  |  | 0
Pipe-run (S) 18, Source: 1, m= 146,5 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  | 2.1 |  |  | 173
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 13
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (R) 18, Source: 1, m= 146,5 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  | 2.1 |  |  | 173
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 17392
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (S) 19, Source: 1, m= 146,3 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  | 0.9 |  |  | 74
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 13
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 6 -

## Components on pipe-runs-5
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| Copper pipes and fittings EN 1057 | Bend 90° 15 - 15 |  | 1.7 |  |  | 80
Pipe-run (R) 19, Source: 1, m= 146,3 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  | 0.9 |  |  | 74
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 17128
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Bend 90° 15 - 15 |  | 1.7 |  |  | 80
Pipe-run (S) 2, Source: 1, m= 691,3 kg/h, Diameter: 28 x 1,5 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 28 mm 40 mm
| Copper pipes and fittings EN 1057 | Tee 35 - 28 - 22 |  | 2 |  |  | 197
| Copper pipes and fittings EN 1057 | Tee 28 - 15 - 22 |  |  |  |  | 0
| Copper pipes and fittings EN 1057 | Elbow 90° 28 - 28 |  | 1.7 |  |  | 131
| Copper pipes and fittings EN 1057 | Elbow 90° 28 - 28 |  | 1.7 |  |  | 131
Pipe-run (R) 2, Source: 1, m= 585,9 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 28 - 35 - 22 |  | 0.6 |  |  | 59
| Copper pipes and fittings EN 1057 | Bend 90° 22 - 22 |  | 1 |  |  | 135
| Copper pipes and fittings EN 1057 | Bend 90° 22 - 22 |  | 1 |  |  | 135
| Copper pipes and fittings EN 1057 | Bend 90° 22 - 22 |  | 1 |  |  | 135
Pipe-run (R) 2_A, Source: 1, m= 585,9 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  |  |  |  | 0
| Copper pipes and fittings EN 1057 | Bend 90° 22 - 22 |  | 1 |  |  | 135
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 7 -

## Components on pipe-runs-6
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 3, Source: 1, m= 105,4 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 28 - 15 - 22 |  | 2.1 |  |  | 162
| Copper pipes and fittings EN 1057 | Tee 15 - 12 - 12 |  |  |  |  | 0
Pipe-run (R) 3, Source: 1, m= 146,6 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  | 2.1 |  |  | 284
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 17315
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (R) 4, Source: 1, m= 439,3 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  | 0.7 |  |  | 95
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  |  |  |  | 0
Pipe-run (S) 4, Source: 1, m= 52,8 kg/h, Diameter: 12 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 12 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 15 - 12 - 12 |  | 2.1 |  |  | 52
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 1"FT - ½"FT |  | 0.4 |  |  | 7
| Brass and steel pipe couplings and fittings | Nipple, straight, imperial ½"MT - ½"MT |  | 0.4 |  |  | 7
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 2
| Copper pipes and fittings EN 1057 | Coupling MT 12 - ½"MT |  | 0.4 |  |  | 7
Pipe-run (S) 5, Source: 1, m= 52,6 kg/h, Diameter: 12 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 12 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 15 - 12 - 12 |  | 0.9 |  |  | 22
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 1"FT - ½"FT |  | 0.4 |  |  | 7
| Brass and steel pipe couplings and fittings | Nipple, straight, imperial ½"MT - ½"MT |  | 0.4 |  |  | 7
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 8 -

## Components on pipe-runs-7
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 2
| Copper pipes and fittings EN 1057 | Coupling MT 12 - ½"MT |  | 0.4 |  |  | 7
| Copper pipes and fittings EN 1057 | Bend 90° 12 - 12 |  | 1.7 |  |  | 30
Pipe-run (R) 5, Source: 1, m= 146,6 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  | 2.1 |  |  | 160
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 17107
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (S) 6, Source: 1, m= 585,9 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 28 - 15 - 22 |  | 0.7 |  |  | 54
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  |  |  |  | 0
Pipe-run (R) 6, Source: 1, m= 292,7 kg/h, Diameter: 18 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 18 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  | 0.7 |  |  | 53
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  |  |  |  | 0
Pipe-run (S) 7, Source: 1, m= 146,6 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  | 2.1 |  |  | 285
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 29
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 13
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 9 -

## Components on pipe-runs-8
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (R) 7, Source: 1, m= 146,5 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  | 2.1 |  |  | 173
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 16594
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
Pipe-run (S) 8, Source: 1, m= 439,3 kg/h, Diameter: 22 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 22 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 22 |  | 0.7 |  |  | 95
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  |  |  |  | 0
Pipe-run (R) 8, Source: 1, m= 146,3 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 18 - 15 - 15 |  | 0.9 |  |  | 74
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 28
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Regulatory automatic balancing valve, FT 15 | DN15 |  | 0 |  | 16330
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Bend 90° 15 - 15 |  | 1.7 |  |  | 80
Pipe-run (R) 9, Source: 1, m= 691,3 kg/h, Diameter: 28 x 1,5 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 28 mm 40 mm
| Copper pipes and fittings EN 1057 | Tee 28 - 35 - 22 |  | 0.6 |  |  | 59
| Copper pipes and fittings EN 1057 | Tee 28 - 12 - 28 |  |  |  |  | 0
| Copper pipes and fittings EN 1057 | Elbow 90° 28 - 28 |  | 1.7 |  |  | 131
| Copper pipes and fittings EN 1057 | Elbow 90° 28 - 28 |  | 1.7 |  |  | 131
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 10 -

## Components on pipe-runs-9
Project: Example of radiant heating installation with radiant ceiling steel panels
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| Copper pipes and fittings EN 1057 | Elbow 90° 28 - 28 |  | 1.7 |  |  | 131
Pipe-run (S) 9, Source: 1, m= 146,6 kg/h, Diameter: 15 x 1,0 mm, Insulation: PE foam lagging, λ(20°C)=0,038W/mK inner diam. 15 mm 25 mm
| Copper pipes and fittings EN 1057 | Tee 22 - 15 - 18 |  | 2.1 |  |  | 160
| Copper pipes and fittings EN 1057 | Coupling FT 22 - 1"FT |  | 0.6 |  |  | 29
| Copper pipes and fittings EN 1057 | Fitting reducer 22 - 15 |  | 0.7 |  |  | 33
| Neutral valves cataloge - typical construction | Ball valve. FT 15, kvs=13.0 | DN15 |  | 13 |  | 13
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
| Copper pipes and fittings EN 1057 | Coupling MT 15 - ½"MT |  | 0.4 |  |  | 19
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 11 -

## General results heating
Project: Example of radiant heating installation with radiant ceiling steel panels
General results heating
No. of sources |  |  | 1
Total number of terminal units |  |  | 10
Total number of pipe-runs |  |  | 39
Total number of manifolds |  |  | 0
Total number of pumps |  |  | 0
Spec. total rooms heat loss ΦH |  |  | 15352 |  | W
Spec. total req. heat output of other TU's |  |  | 0 |  | W
Spec. total rooms req. heat output Φreq |  |  | 15352 |  | W
Calculation standards:
Radiators sizing standard |  |  | EN 442-2
Floor heating standard |  |  | EN 1264: 1:2011 2:2013 3,4:2009 5:2008
Wall and ceiling panels calculation standard |  |  | EN 14037
Source: Plate type exchanger: 1, Application: Heating systems/Cooling systems, Medium: Water
| Source elevation |  | 0.3 |  | m
| Supply and return temperature |  | 45,0 / 38,7 |  | °C
| Total output |  | 9280 |  | W
| Total output of convectors Φconv,H |  | 0 |  | W
| Total output of radiant heaters Φrh,H |  | 9008 |  | W
| Total output of other heaters |  | 0 |  | W
| Heat gains from pipe-runs accounted for in balance |  | 0 |  | W
| Not utilized heat loss of pipe-runs |  | 272 |  | W
| Losses of radiant systems to outside of source feed area |  | 0 |  | W
| Losses of radiant systems within source feed area |  | 0 |  | W
| Available pressure |  | 24.4 |  | kPa
| Pressure drop along critical route |  | 24.5 |  | kPa
| Pressure drop on critical terminal unit |  | 0.2 |  | kPa
| Press. drop on source |  | 0 |  | kPa
| Flow rate in source |  | 1277.3 |  | kg/h
| Critical receptor: | 0.8-10
| Critical TU route length |  | 37.9 |  | m
| Capacity of system incl. terminal units |  | 93.8 |  | dm³
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 |  |  |  | - 12 -

## Radiant heating general res
Project: Example of radiant heating installation with radiant ceiling steel panels
Radiant heating general results
Source/Source: 1 |  |  | Application: Heating systems/Cooling systems |  | Medium: Water
Temperatures θs,H and θr,H [°C] |  | 45 |  | 38.7
Temperature source for control circuits | Source/1
Temperatures θs,H and θr,H [°C] |  | 45 |  | 38.7
Required heating output Φreq,H [W] |  | 9078
Obtained heating output ΦH [W] |  | 9008
Heat capacity lost ΦOS,H [W] |  | 0
Mass flow rate m [kg/h] |  | 1277.3
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 13 -

## Heating terminal units
Project: Example of radiant heating installation with radiant ceiling steel panels
Heating terminal units
Terminal unit symbol |  |  |  | Room symbol |  | Room temperature | Specified terminal unit output | Sized terminal unit output | Mass flow rate | Supply temperature | Return temperature | Type | Length | Height / Width |  | Depth / Thickness | Terminal unit oversizing or undersizing percentage
Terminal unit |  |  |  | Room |  | θi,H | Φreq,H | ΦH | m | θs,H | θr,H | Type | L | H/W |  | D | A'/A
[6 empty] | °C | W | W | kg/h | °C | °C |  | mm | mm |  | mm | %
Storey: |  | 1 | Building unit: |  | 1
| 0.8-1 |  |  | 0.8 |  | 20 | 1025 | 1018 | 146.3 | 44.9 | 38.9 | Ceiling steel panel Type-1 (0,32m) | 14000 | 55 |  | 320 | 99
| 0.8-10 |  |  | 0.8 |  | 20 | 1025 | 1017 | 146.3 | 44.9 | 38.9 | Ceiling steel panel Type-1 (0,32m) | 14000 | 55 |  | 320 | 99
| 0.8-2 |  |  | 0.8 |  | 20 | 1025 | 1019 | 146.5 | 44.9 | 38.9 | Ceiling steel panel Type-1 (0,32m) | 14000 | 55 |  | 320 | 99
| 0.8-3 |  |  | 0.8 |  | 20 | 1025 | 1020 | 146.6 | 44.9 | 38.9 | Ceiling steel panel Type-1 (0,32m) | 14000 | 55 |  | 320 | 99
| 0.8-4 |  |  | 0.8 |  | 20 | 1025 | 1020 | 146.7 | 45 | 39 | Ceiling steel panel Type-1 (0,32m) | 14000 | 55 |  | 320 | 100
| 0.8-5 |  |  | 0.8 |  | 20 | 439 | 429 | 52.8 | 44.9 | 37.9 | Ceiling steel panel Type-1 (0,32m) | 6000 | 55 |  | 320 | 98
| 0.8-6 |  |  | 0.8 |  | 20 | 439 | 427 | 52.6 | 44.8 | 37.8 | Ceiling steel panel Type-1 (0,32m) | 6000 | 55 |  | 320 | 97
| 0.8-7 |  |  | 0.8 |  | 20 | 1025 | 1020 | 146.6 | 45 | 39 | Ceiling steel panel Type-1 (0,32m) | 14000 | 55 |  | 320 | 100
| 0.8-8 |  |  | 0.8 |  | 20 | 1025 | 1019 | 146.5 | 44.9 | 38.9 | Ceiling steel panel Type-1 (0,32m) | 14000 | 55 |  | 320 | 99
| 0.8-9 |  |  | 0.8 |  | 20 | 1025 | 1020 | 146.6 | 44.9 | 38.9 | Ceiling steel panel Type-1 (0,32m) | 14000 | 55 |  | 320 | 99
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [14 empty] | - 14 -

## Heating pipe-runs
Project: Example of radiant heating installation with radiant ceiling steel panels
Heating pipe-runs
Pipe-run type |  | Pipe-run no. |  |  | Connection piperun No. | Heat quantity carried by pipe-run | Diameter | Length | Specific friction resistance |  | Total friction loss |  | Total loss | Flow velocity |  | Mass flow rate |  | Insulation thickness |  | Inlet temperature | Specific heat loss in pipe-run
Type |  | Pipe-run symbol |  |  | Symbol of conn. pipes | ΦH | Diam. | L | R |  | ζ |  | Tot. press. drop | v |  | m |  | Insul. |  | θinlet,H | qH
[6 empty] | W | mm | m | Pa/m |  |  |  | Pa | m/s |  | kg/h |  | mm |  | °C | W/m
Source: |  |  | 1
| S | 1 |  |  | Source: 1 | 9008 | 35 x 1,5 | 2.34 | 76 |  | 3.3 |  | 502 | 0.45 |  | 1277.3 |  | 40 |  | 45 | 4.53
| R | 1 |  |  | Source: 1 | 9008 | 35 x 1,5 | 2.53 | 78 |  | 1.7 |  | 363 | 0.44 |  | 1277.3 |  | 40 |  | 38.7 | 3.36
| S | 2 |  |  | 1 | 4931 | 28 x 1,5 | 4.13 | 83 |  | 5.4 |  | 803 | 0.4 |  | 691.3 |  | 40 |  | 45 | 4.04
| R | 2 |  |  | 1 | 4076 | 22 x 1,0 | 8.51 | 185 |  | 3.6 |  | 2035 | 0.52 |  | 585.9 |  | 25 |  | 38.9 | 3.2
| R | 2_A |  |  | 2 | 4076 | 22 x 1,0 | 11.12 | 184 |  | 1 |  | 2186 | 0.52 |  | 585.9 |  | 25 |  | 38.9 | 3.21
| S | 3 |  |  | 2 | 855 | 15 x 1,0 | 3.25 | 69 |  | 2.1 |  | 386 | 0.22 |  | 105.4 |  | 25 |  | 45 | 3.55
| R | 3 |  |  | 2_A | 1020 | 15 x 1,0 | 0.46 | 126 |  | 4.2 |  | 17757 | 0.31 |  | 146.6 |  | 25 |  | 39 | 2.67
|  |  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[10 empty] | mm |  | kPa
|  |  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 17.32 |  |  | 0 |  | 0 |  | 144,50 l/h
| R | 4 |  |  | 2_A | 3056 | 22 x 1,0 | 1.22 | 111 |  | 0.7 |  | 230 | 0.39 |  | 439.3 |  | 25 |  | 38.9 | 3.22
| S | 4 |  |  | 3 | 429 | 12 x 1,0 | 0.22 | 72 |  | 3.3 |  | 90 | 0.19 |  | 52.8 |  | 25 |  | 44.9 | 3.2
|  |  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[10 empty] | mm |  | kPa
|  |  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0 |  |  | 0 |  | 0
| S | 5 |  |  | 3 | 427 | 12 x 1,0 | 1.74 | 71 |  | 3.8 |  | 199 | 0.19 |  | 52.6 |  | 25 |  | 44.9 | 3.2
|  |  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[10 empty] | mm |  | kPa
|  |  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0 |  |  | 0 |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [19 empty] | - 15 -

## Heating pipe-runs-1
Project: Example of radiant heating installation with radiant ceiling steel panels
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R |  | ζ |  | Tot. press. drop | v |  | m |  | Insul. |  | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  |  |  | Pa | m/s |  | kg/h |  | mm |  | °C | W/m
| R | 5 |  | 4 | 1020 | 15 x 1,0 | 0.46 | 126 |  | 4.2 |  | 17424 | 0.31 |  | 146.6 |  | 25 |  | 38.9 | 2.67
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 17.11 |  |  | 0 |  | 0 |  | 144,50 l/h
| S | 6 |  | 2 | 4076 | 22 x 1,0 | 0.99 | 180 |  | 0.7 |  | 232 | 0.52 |  | 585.9 |  | 25 |  | 45 | 4.3
| R | 6 |  | 4 | 2036 | 18 x 1,0 | 1.22 | 158 |  | 0.7 |  | 245 | 0.41 |  | 292.7 |  | 25 |  | 38.9 | 2.9
| S | 7 |  | 6 | 1020 | 15 x 1,0 | 0.49 | 123 |  | 4.2 |  | 458 | 0.31 |  | 146.6 |  | 25 |  | 45 | 3.56
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0.01 |  |  | 0 |  | 0
| R | 7 |  | 6 | 1019 | 15 x 1,0 | 0.49 | 126 |  | 4.2 |  | 16929 | 0.31 |  | 146.5 |  | 25 |  | 38.9 | 2.67
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 16.59 |  |  | 0 |  | 0 |  | 144,50 l/h
| S | 8 |  | 6 | 3056 | 22 x 1,0 | 1.22 | 109 |  | 0.7 |  | 227 | 0.39 |  | 439.3 |  | 25 |  | 45 | 4.3
| R | 8 |  | 6 | 1017 | 15 x 1,0 | 1.68 | 125 |  | 4.7 |  | 16795 | 0.31 |  | 146.3 |  | 25 |  | 38.9 | 2.66
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 16.33 |  |  | 0 |  | 0 |  | 144,50 l/h
| R | 9 |  | 1 | 4932 | 28 x 1,5 | 6.18 | 85 |  | 5.7 |  | 980 | 0.39 |  | 691.3 |  | 40 |  | 38.7 | 2.99
| S | 9 |  | 8 | 1020 | 15 x 1,0 | 0.49 | 123 |  | 4.2 |  | 333 | 0.31 |  | 146.6 |  | 25 |  | 45 | 3.56
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0.01 |  |  | 0 |  | 0
| S | 10 |  | 8 | 2036 | 18 x 1,0 | 1.22 | 154 |  | 0.7 |  | 241 | 0.41 |  | 292.7 |  | 25 |  | 45 | 3.88
| R | 10 |  | 9 | 429 | 12 x 1,0 | 0.19 | 74 |  | 3.3 |  | 21347 | 0.19 |  | 52.8 |  | 25 |  | 37.9 | 2.27
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 21.15 |  |  | 0 |  | 0 |  | 50,00 l/h
| R | 11 |  | 9 | 4503 | 28 x 1,5 | 1.52 | 74 |  | 0.7 |  | 167 | 0.36 |  | 638.5 |  | 40 |  | 38.8 | 3
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [18 empty] | - 16 -

## Heating pipe-runs-2
Project: Example of radiant heating installation with radiant ceiling steel panels
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R |  | ζ |  | Tot. press. drop | v |  | m |  | Insul. |  | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  |  |  | Pa | m/s |  | kg/h |  | mm |  | °C | W/m
| S | 11 |  | 10 | 1019 | 15 x 1,0 | 0.46 | 123 |  | 4.2 |  | 342 | 0.31 |  | 146.5 |  | 25 |  | 44.9 | 3.55
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0.01 |  |  | 0 |  | 0
| S | 12 |  | 10 | 1017 | 15 x 1,0 | 1.71 | 122 |  | 4.7 |  | 476 | 0.31 |  | 146.3 |  | 25 |  | 44.9 | 3.55
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0.01 |  |  | 0 |  | 0
| R | 12 |  | 11 | 427 | 12 x 1,0 | 0.19 | 74 |  | 3.3 |  | 21073 | 0.19 |  | 52.6 |  | 25 |  | 37.8 | 2.26
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 20.9 |  |  | 0 |  | 0 |  | 50,00 l/h
| S | 13 |  | 1 | 4076 | 22 x 1,0 | 4.06 | 180 |  | 2.7 |  | 1072 | 0.52 |  | 586 |  | 25 |  | 45 | 4.3
| R | 13 |  | 11 | 4076 | 22 x 1,0 | 11.13 | 185 |  | 1.7 |  | 2235 | 0.52 |  | 586 |  | 25 |  | 38.9 | 3.21
| S | 14 |  | 13 | 1020 | 15 x 1,0 | 0.49 | 123 |  | 4.2 |  | 457 | 0.31 |  | 146.7 |  | 25 |  | 45 | 3.56
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0.01 |  |  | 0 |  | 0
| R | 14 |  | 13 | 1020 | 15 x 1,0 | 0.49 | 126 |  | 4.2 |  | 18559 | 0.31 |  | 146.7 |  | 25 |  | 39 | 2.67
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 18.11 |  |  | 0 |  | 0 |  | 144,50 l/h
| S | 15 |  | 13 | 3056 | 22 x 1,0 | 1.22 | 109 |  | 0.7 |  | 227 | 0.39 |  | 439.3 |  | 25 |  | 45 | 4.3
| R | 15 |  | 13 | 3056 | 22 x 1,0 | 1.22 | 111 |  | 0.7 |  | 231 | 0.39 |  | 439.3 |  | 25 |  | 38.9 | 3.22
| S | 16 |  | 15 | 1020 | 15 x 1,0 | 0.49 | 123 |  | 4.2 |  | 332 | 0.31 |  | 146.6 |  | 25 |  | 45 | 3.56
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0.01 |  |  | 0 |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [18 empty] | - 17 -

## Heating pipe-runs-3
Project: Example of radiant heating installation with radiant ceiling steel panels
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R |  | ζ |  | Tot. press. drop | v |  | m |  | Insul. |  | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  |  |  | Pa | m/s |  | kg/h |  | mm |  | °C | W/m
| R | 16 |  | 15 | 1020 | 15 x 1,0 | 0.49 | 126 |  | 4.2 |  | 18226 | 0.31 |  | 146.6 |  | 25 |  | 38.9 | 2.67
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 17.9 |  |  | 0 |  | 0 |  | 144,50 l/h
| S | 17 |  | 15 | 2036 | 18 x 1,0 | 1.22 | 154 |  | 0.7 |  | 241 | 0.41 |  | 292.7 |  | 25 |  | 45 | 3.88
| R | 17 |  | 15 | 2036 | 18 x 1,0 | 1.22 | 158 |  | 0.7 |  | 246 | 0.41 |  | 292.7 |  | 25 |  | 38.9 | 2.9
| S | 18 |  | 17 | 1019 | 15 x 1,0 | 0.49 | 123 |  | 4.2 |  | 346 | 0.31 |  | 146.5 |  | 25 |  | 44.9 | 3.55
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0.01 |  |  | 0 |  | 0
| R | 18 |  | 17 | 1019 | 15 x 1,0 | 0.49 | 126 |  | 4.2 |  | 17726 | 0.31 |  | 146.5 |  | 25 |  | 38.9 | 2.67
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 17.39 |  |  | 0 |  | 0 |  | 144,50 l/h
| S | 19 |  | 17 | 1018 | 15 x 1,0 | 1.71 | 122 |  | 4.7 |  | 476 | 0.31 |  | 146.3 |  | 25 |  | 44.9 | 3.55
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Ball valve. FT 15, kvs=13.0 | [5 empty] | 15 |  | 0.01 |  |  | 0 |  | 0
| R | 19 |  | 17 | 1018 | 15 x 1,0 | 1.71 | 126 |  | 4.7 |  | 17596 | 0.31 |  | 146.3 |  | 25 |  | 38.9 | 2.66
|  |  | Type | [5 empty] | Diameter |  | Thermal resistance |  |  | Xp |  | A |  | Setting
[9 empty] | mm |  | kPa
|  |  | Regulatory automatic balancing valve, FT 15 | [5 empty] | 15 |  | 17.13 |  |  | 0 |  | 0 |  | 144,50 l/h
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [18 empty] | - 18 -

## List of rooms - heating
Project: Example of radiant heating installation with radiant ceiling steel panels
List of rooms - heating
Room Symbol |  |  |  |  | Room surface area | Thermal resistance of covering |  | Design room temperature | Heat loss in room | Required output of heating | Required specific heating output | Required radiant heating output | Required convection heating output | Obtained radiant heating output | Obtained convection heating output | Output recovered from pipe-runs | Coverage of required heating output
Room |  |  |  |  | A | Rλ,B |  | θi,H | Φstd,H | Φreq,H | qreq,H | Φreq,rad,H | Φreq,conv,H | Φrh,H | Φconv,H | Φpipe,H | %Φreq,H
[5 empty] | m² | (m²·K)/W |  | °C | W | W | W/m² | W | W | W | W | W | %
Storey: |  | 0, | Elevation |  |  |  | -2,8 m
| Bld. unit: |  |  | 01
| 0.10-basement |  |  |  | 18.4 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.11-basement |  |  |  | 18.4 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.12-basement |  |  |  | 23.7 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.13-basement |  |  |  | 33.1 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.14-basement |  |  |  | 33.1 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.1-basement |  |  |  | 23.6 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.2-basement |  |  |  | 18.4 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.3-basement |  |  |  | 18.4 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.4-basement |  |  |  | 23.6 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.5-basement |  |  |  | 10.1 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.6-basement |  |  |  | 119.6 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.7-basement |  |  |  | 9.2 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.8-basement |  |  |  | 6.6 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
| 0.9-basement |  |  |  | 23.7 |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ???
Storey: |  | 1, | Elevation |  |  |  | 0 m
| Bld. unit: |  |  | 01
| 0.1 |  |  |  | 98.3 |  |  | 20 | 5404 | 4421 | 45 | 0 | 4421 | 0 | 0 | 0 | 0
| 0.10 |  |  |  | 2.9 |  |  | 20 | 0 | 130 | 45 | 0 | 130 | 0 | 0 | 0 | 0
| 0.11 |  |  |  | 3.3 |  |  | 20 | 0 | 150 | 45 | 0 | 150 | 0 | 0 | 0 | 0
| 0.6 |  |  |  | 29.2 |  |  | 20 | 1606 | 1314 | 45 | 0 | 1314 | 0 | 0 | 0 | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [15 empty] | - 19 -

## List of rooms - heating-1
Project: Example of radiant heating installation with radiant ceiling steel panels
Room |  | A | Rλ,B | θi,H | Φstd,H | Φreq,H | qreq,H | Φreq,rad,H | Φreq,conv,H | Φrh,H | Φconv,H | Φpipe,H | %Φreq,H
|  | m² | (m²·K)/W | °C | W | W | W/m² | W | W | W | W | W | %
| 0.8 | 201.7 |  | 20 | 0 | 9078 | 45 | 9078 | 0 | 9008 | 0 | 0 | 99
| 0.9 | 5.7 |  | 20 | 0 | 258 | 45 | 0 | 258 | 0 | 0 | 0 | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [11 empty] | - 20 -

## Heating_cooling circuits
Project: Example of radiant heating installation with radiant ceiling steel panels
Heating/cooling circuits
Label |  | Symbol |  | ΦH | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Ceiling panel: |  |  | 0.8-5
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 2 |  | 4931 | 691.3 | 28 x 1,5 | 4.13 | 0.4 | 83 | 5.4 | 459 | 803 | 0 |  | 803 | 40
|  | 3 |  | 855 | 105.4 | 15 x 1,0 | 3.25 | 0.22 | 69 | 2.1 | 162 | 386 | 0 |  | 386 | 25
|  | 4 |  | 429 | 52.8 | 12 x 1,0 | 0.22 | 0.19 | 72 | 3.3 | 73 | 89 | 2 |  | 90 | 25
| Ceiling panel | 0.8-5 |  | 429 | 52.8 | [7 empty] | 0 |  | 24
| Ceiling panel (Thermosiphon) | [13 empty] | -49
|  | 10 |  | 429 | 52.8 | 12 x 1,0 | 0.19 | 0.19 | 74 | 3.3 | 183 | 197 | 21150 |  | 21347 | 25
|  | 9 |  | 4932 | 691.3 | 28 x 1,5 | 6.18 | 0.39 | 85 | 5.7 | 452 | 980 | 0 |  | 980 | 40
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-6
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 2 |  | 4931 | 691.3 | 28 x 1,5 | 4.13 | 0.4 | 83 | 5.4 | 459 | 803 | 0 |  | 803 | 40
|  | 3 |  | 855 | 105.4 | 15 x 1,0 | 3.25 | 0.22 | 69 | 2.1 | 162 | 386 | 0 |  | 386 | 25
|  | 5 |  | 427 | 52.6 | 12 x 1,0 | 1.74 | 0.19 | 71 | 3.8 | 73 | 197 | 2 |  | 199 | 25
| Ceiling panel | 0.8-6 |  | 427 | 52.6 | [7 empty] | 0 |  | 23
| Ceiling panel (Thermosiphon) | [13 empty] | -49
|  | 12 |  | 427 | 52.6 | 12 x 1,0 | 0.19 | 0.19 | 74 | 3.3 | 159 | 173 | 20900 |  | 21073 | 25
|  | 11 |  | 4503 | 638.5 | 28 x 1,5 | 1.52 | 0.36 | 74 | 0.7 | 54 | 167 | 0 |  | 167 | 40
|  | 9 |  | 4932 | 691.3 | 28 x 1,5 | 6.18 | 0.39 | 85 | 5.7 | 452 | 980 | 0 |  | 980 | 40
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-4
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 13 |  | 4076 | 586 | 22 x 1,0 | 4.06 | 0.52 | 180 | 2.7 | 340 | 1072 | 0 |  | 1072 | 25
|  | 14 |  | 1020 | 146.7 | 15 x 1,0 | 0.49 | 0.31 | 123 | 4.2 | 385 | 444 | 13 |  | 457 | 25
| Ceiling panel | 0.8-4 |  | 1020 | 146.7 | [7 empty] | 0 |  | 158
| Ceiling panel (Thermosiphon) | [13 empty] | -45
|  | 14 |  | 1020 | 146.7 | 15 x 1,0 | 0.49 | 0.31 | 126 | 4.2 | 384 | 446 | 18113 |  | 18559 | 25
|  | 13 |  | 4076 | 586 | 22 x 1,0 | 11.13 | 0.52 | 185 | 1.7 | 181 | 2235 | 0 |  | 2235 | 25
|  | 11 |  | 4503 | 638.5 | 28 x 1,5 | 1.52 | 0.36 | 74 | 0.7 | 54 | 167 | 0 |  | 167 | 40
|  | 9 |  | 4932 | 691.3 | 28 x 1,5 | 6.18 | 0.39 | 85 | 5.7 | 452 | 980 | 0 |  | 980 | 40
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [13 empty] | - 21 -

## Heating_cooling circuits-1
Project: Example of radiant heating installation with radiant ceiling steel panels
Label |  | Symbol |  | ΦH | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-7
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 2 |  | 4931 | 691.3 | 28 x 1,5 | 4.13 | 0.4 | 83 | 5.4 | 459 | 803 | 0 |  | 803 | 40
|  | 6 |  | 4076 | 585.9 | 22 x 1,0 | 0.99 | 0.52 | 180 | 0.7 | 54 | 232 | 0 |  | 232 | 25
|  | 7 |  | 1020 | 146.6 | 15 x 1,0 | 0.49 | 0.31 | 123 | 4.2 | 385 | 445 | 13 |  | 458 | 25
| Ceiling panel | 0.8-7 |  | 1020 | 146.6 | [7 empty] | 0 |  | 158
| Ceiling panel (Thermosiphon) | [13 empty] | -45
|  | 3 |  | 1020 | 146.6 | 15 x 1,0 | 0.46 | 0.31 | 126 | 4.2 | 384 | 441 | 17315 |  | 17757 | 25
|  | 2_A |  | 4076 | 585.9 | 22 x 1,0 | 11.12 | 0.52 | 184 | 1 | 135 | 2186 | 0 |  | 2186 | 25
|  | 2 |  | 4076 | 585.9 | 22 x 1,0 | 8.51 | 0.52 | 185 | 3.6 | 464 | 2035 | 0 |  | 2035 | 25
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-3
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 13 |  | 4076 | 586 | 22 x 1,0 | 4.06 | 0.52 | 180 | 2.7 | 340 | 1072 | 0 |  | 1072 | 25
|  | 15 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 109 | 0.7 | 95 | 227 | 0 |  | 227 | 25
|  | 16 |  | 1020 | 146.6 | 15 x 1,0 | 0.49 | 0.31 | 123 | 4.2 | 260 | 319 | 13 |  | 332 | 25
| Ceiling panel | 0.8-3 |  | 1020 | 146.6 | [7 empty] | 0 |  | 158
| Ceiling panel (Thermosiphon) | [13 empty] | -45
|  | 16 |  | 1020 | 146.6 | 15 x 1,0 | 0.49 | 0.31 | 126 | 4.2 | 259 | 321 | 17904 |  | 18226 | 25
|  | 15 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 111 | 0.7 | 95 | 231 | 0 |  | 231 | 25
|  | 13 |  | 4076 | 586 | 22 x 1,0 | 11.13 | 0.52 | 185 | 1.7 | 181 | 2235 | 0 |  | 2235 | 25
|  | 11 |  | 4503 | 638.5 | 28 x 1,5 | 1.52 | 0.36 | 74 | 0.7 | 54 | 167 | 0 |  | 167 | 40
|  | 9 |  | 4932 | 691.3 | 28 x 1,5 | 6.18 | 0.39 | 85 | 5.7 | 452 | 980 | 0 |  | 980 | 40
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-9
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 2 |  | 4931 | 691.3 | 28 x 1,5 | 4.13 | 0.4 | 83 | 5.4 | 459 | 803 | 0 |  | 803 | 40
|  | 6 |  | 4076 | 585.9 | 22 x 1,0 | 0.99 | 0.52 | 180 | 0.7 | 54 | 232 | 0 |  | 232 | 25
|  | 8 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 109 | 0.7 | 95 | 227 | 0 |  | 227 | 25
|  | 9 |  | 1020 | 146.6 | 15 x 1,0 | 0.49 | 0.31 | 123 | 4.2 | 260 | 320 | 13 |  | 333 | 25
| Ceiling panel | 0.8-9 |  | 1020 | 146.6 | [7 empty] | 0 |  | 158
| Ceiling panel (Thermosiphon) | [13 empty] | -45
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [13 empty] | - 22 -

## Heating_cooling circuits-2
Project: Example of radiant heating installation with radiant ceiling steel panels
Label |  | Symbol |  | ΦH | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 5 |  | 1020 | 146.6 | 15 x 1,0 | 0.46 | 0.31 | 126 | 4.2 | 259 | 317 | 17107 |  | 17424 | 25
|  | 4 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 111 | 0.7 | 95 | 230 | 0 |  | 230 | 25
|  | 2_A |  | 4076 | 585.9 | 22 x 1,0 | 11.12 | 0.52 | 184 | 1 | 135 | 2186 | 0 |  | 2186 | 25
|  | 2 |  | 4076 | 585.9 | 22 x 1,0 | 8.51 | 0.52 | 185 | 3.6 | 464 | 2035 | 0 |  | 2035 | 25
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-2
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 13 |  | 4076 | 586 | 22 x 1,0 | 4.06 | 0.52 | 180 | 2.7 | 340 | 1072 | 0 |  | 1072 | 25
|  | 15 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 109 | 0.7 | 95 | 227 | 0 |  | 227 | 25
|  | 17 |  | 2036 | 292.7 | 18 x 1,0 | 1.22 | 0.41 | 154 | 0.7 | 53 | 241 | 0 |  | 241 | 25
|  | 18 |  | 1019 | 146.5 | 15 x 1,0 | 0.49 | 0.31 | 123 | 4.2 | 273 | 333 | 13 |  | 346 | 25
| Ceiling panel | 0.8-2 |  | 1019 | 146.5 | [7 empty] | 0 |  | 158
| Ceiling panel (Thermosiphon) | [13 empty] | -45
|  | 18 |  | 1019 | 146.5 | 15 x 1,0 | 0.49 | 0.31 | 126 | 4.2 | 272 | 334 | 17392 |  | 17726 | 25
|  | 17 |  | 2036 | 292.7 | 18 x 1,0 | 1.22 | 0.41 | 158 | 0.7 | 53 | 246 | 0 |  | 246 | 25
|  | 15 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 111 | 0.7 | 95 | 231 | 0 |  | 231 | 25
|  | 13 |  | 4076 | 586 | 22 x 1,0 | 11.13 | 0.52 | 185 | 1.7 | 181 | 2235 | 0 |  | 2235 | 25
|  | 11 |  | 4503 | 638.5 | 28 x 1,5 | 1.52 | 0.36 | 74 | 0.7 | 54 | 167 | 0 |  | 167 | 40
|  | 9 |  | 4932 | 691.3 | 28 x 1,5 | 6.18 | 0.39 | 85 | 5.7 | 452 | 980 | 0 |  | 980 | 40
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-8
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 2 |  | 4931 | 691.3 | 28 x 1,5 | 4.13 | 0.4 | 83 | 5.4 | 459 | 803 | 0 |  | 803 | 40
|  | 6 |  | 4076 | 585.9 | 22 x 1,0 | 0.99 | 0.52 | 180 | 0.7 | 54 | 232 | 0 |  | 232 | 25
|  | 8 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 109 | 0.7 | 95 | 227 | 0 |  | 227 | 25
|  | 10 |  | 2036 | 292.7 | 18 x 1,0 | 1.22 | 0.41 | 154 | 0.7 | 53 | 241 | 0 |  | 241 | 25
|  | 11 |  | 1019 | 146.5 | 15 x 1,0 | 0.46 | 0.31 | 123 | 4.2 | 273 | 329 | 13 |  | 342 | 25
| Ceiling panel | 0.8-8 |  | 1019 | 146.5 | [7 empty] | 0 |  | 158
| Ceiling panel (Thermosiphon) | [13 empty] | -45
|  | 7 |  | 1019 | 146.5 | 15 x 1,0 | 0.49 | 0.31 | 126 | 4.2 | 272 | 334 | 16594 |  | 16929 | 25
|  | 6 |  | 2036 | 292.7 | 18 x 1,0 | 1.22 | 0.41 | 158 | 0.7 | 53 | 245 | 0 |  | 245 | 25
|  | 4 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 111 | 0.7 | 95 | 230 | 0 |  | 230 | 25
|  | 2_A |  | 4076 | 585.9 | 22 x 1,0 | 11.12 | 0.52 | 184 | 1 | 135 | 2186 | 0 |  | 2186 | 25
|  | 2 |  | 4076 | 585.9 | 22 x 1,0 | 8.51 | 0.52 | 185 | 3.6 | 464 | 2035 | 0 |  | 2035 | 25
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-1
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [13 empty] | - 23 -

## Heating_cooling circuits-3
Project: Example of radiant heating installation with radiant ceiling steel panels
Label |  | Symbol |  | ΦH | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 13 |  | 4076 | 586 | 22 x 1,0 | 4.06 | 0.52 | 180 | 2.7 | 340 | 1072 | 0 |  | 1072 | 25
|  | 15 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 109 | 0.7 | 95 | 227 | 0 |  | 227 | 25
|  | 17 |  | 2036 | 292.7 | 18 x 1,0 | 1.22 | 0.41 | 154 | 0.7 | 53 | 241 | 0 |  | 241 | 25
|  | 19 |  | 1018 | 146.3 | 15 x 1,0 | 1.71 | 0.31 | 122 | 4.7 | 254 | 463 | 13 |  | 476 | 25
| Ceiling panel | 0.8-1 |  | 1018 | 146.3 | [7 empty] | 0 |  | 157
| Ceiling panel (Thermosiphon) | [13 empty] | -45
|  | 19 |  | 1018 | 146.3 | 15 x 1,0 | 1.71 | 0.31 | 126 | 4.7 | 254 | 468 | 17128 |  | 17596 | 25
|  | 17 |  | 2036 | 292.7 | 18 x 1,0 | 1.22 | 0.41 | 158 | 0.7 | 53 | 246 | 0 |  | 246 | 25
|  | 15 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 111 | 0.7 | 95 | 231 | 0 |  | 231 | 25
|  | 13 |  | 4076 | 586 | 22 x 1,0 | 11.13 | 0.52 | 185 | 1.7 | 181 | 2235 | 0 |  | 2235 | 25
|  | 11 |  | 4503 | 638.5 | 28 x 1,5 | 1.52 | 0.36 | 74 | 0.7 | 54 | 167 | 0 |  | 167 | 40
|  | 9 |  | 4932 | 691.3 | 28 x 1,5 | 6.18 | 0.39 | 85 | 5.7 | 452 | 980 | 0 |  | 980 | 40
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
Circuit through Ceiling panel: |  |  | 0.8-10
| Source | 1 |  | 9280 | 1277.3 | [9 empty] | 0
| Source (H avail.) | [13 empty] | -24447
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.34 | 0.45 | 76 | 3.3 | 324 | 502 | 0 |  | 502 | 40
|  | 2 |  | 4931 | 691.3 | 28 x 1,5 | 4.13 | 0.4 | 83 | 5.4 | 459 | 803 | 0 |  | 803 | 40
|  | 6 |  | 4076 | 585.9 | 22 x 1,0 | 0.99 | 0.52 | 180 | 0.7 | 54 | 232 | 0 |  | 232 | 25
|  | 8 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 109 | 0.7 | 95 | 227 | 0 |  | 227 | 25
|  | 10 |  | 2036 | 292.7 | 18 x 1,0 | 1.22 | 0.41 | 154 | 0.7 | 53 | 241 | 0 |  | 241 | 25
|  | 12 |  | 1017 | 146.3 | 15 x 1,0 | 1.71 | 0.31 | 122 | 4.7 | 254 | 463 | 13 |  | 476 | 25
| Ceiling panel | 0.8-10 |  | 1017 | 146.3 | [7 empty] | 0 |  | 157
| Ceiling panel (Thermosiphon) | [13 empty] | -45
|  | 8 |  | 1017 | 146.3 | 15 x 1,0 | 1.68 | 0.31 | 125 | 4.7 | 253 | 464 | 16330 |  | 16795 | 25
|  | 6 |  | 2036 | 292.7 | 18 x 1,0 | 1.22 | 0.41 | 158 | 0.7 | 53 | 245 | 0 |  | 245 | 25
|  | 4 |  | 3056 | 439.3 | 22 x 1,0 | 1.22 | 0.39 | 111 | 0.7 | 95 | 230 | 0 |  | 230 | 25
|  | 2_A |  | 4076 | 585.9 | 22 x 1,0 | 11.12 | 0.52 | 184 | 1 | 135 | 2186 | 0 |  | 2186 | 25
|  | 2 |  | 4076 | 585.9 | 22 x 1,0 | 8.51 | 0.52 | 185 | 3.6 | 464 | 2035 | 0 |  | 2035 | 25
|  | 1 |  | 9008 | 1277.3 | 35 x 1,5 | 2.53 | 0.44 | 78 | 1.7 | 167 | 363 | 0 |  | 363 | 40
[13 empty] | Total: |  | 0
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [13 empty] | - 24 -

## List of pipes, pipe fitting
Project: Example of radiant heating installation with radiant ceiling steel panels
List of pipes, pipe fittings and couplings
Product |  | Size | Catalogue code |  | Qty. | Unit
Brass and steel pipe couplings and fittings
Pipe fittings
| Female connector, reduction, imperial | 1"FT - ½"FT |  |  | 4 | pcs.
| Flange PN16 | F40 PN16 | DN40_16 |  | 2 | pcs.
| Nipple, straight, imperial | ½"MT - ½"MT |  |  | 4 | pcs.
Copper pipes and fittings EN 1057
Pipes
| Hard copper pipe, Type X bars | 28 x 1,5 |  |  | 12 | m
| Hard copper pipe, Type X bars | 35 x 1,5 |  |  | 5 | m
| Soft copper pipe, Type X coils | 12 x 1 |  |  | 3 | m
| Soft copper pipe, Type X coils | 15 x 1 |  |  | 16 | m
| Soft copper pipe, Type X coils | 18 x 1 |  |  | 5 | m
| Soft copper pipe, Type X coils | 22 x 1 |  |  | 41 | m
Pipe fittings
| Bend 90° | 12 - 12 |  |  | 1 | pcs.
| Bend 90° | 15 - 15 |  |  | 4 | pcs.
| Bend 90° | 22 - 22 |  |  | 7 | pcs.
| Coupling FT | 22 - 1"FT |  |  | 16 | pcs.
| Coupling MT | 12 - ½"MT |  |  | 4 | pcs.
| Coupling MT | 15 - ½"MT |  |  | 32 | pcs.
| Coupling MT | 35 - 1½"MT |  |  | 2 | pcs.
| Elbow 90° | 28 - 28 |  |  | 5 | pcs.
| Elbow 90° | 35 - 35 |  |  | 3 | pcs.
| Fitting reducer | 22 - 15 |  |  | 16 | pcs.
| Tee | 28 - 15 - 22 |  |  | 1 | pcs.
| Tee | 28 - 35 - 22 |  |  | 1 | pcs.
| Tee | 15 - 12 - 12 |  |  | 1 | pcs.
| Tee | 35 - 28 - 22 |  |  | 1 | pcs.
| Tee | 18 - 15 - 15 |  |  | 4 | pcs.
| Tee | 22 - 15 - 18 |  |  | 4 | pcs.
| Tee | 22 - 15 - 22 |  |  | 4 | pcs.
| Tee | 28 - 12 - 22 |  |  | 1 | pcs.
| Tee | 28 - 12 - 28 |  |  | 1 | pcs.
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 |  |  |  | - 25 -

## List of pipes, pipe fitting-1
Project: Example of radiant heating installation with radiant ceiling steel panels
List of insulation
Product |  | Size | Catalogue code |  | Qty. | Unit
Standard insulation catalogue
Lagging
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=12 mm, Th=25 mm |  |  | 3 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=15 mm, Th=25 mm |  |  | 16 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=18 mm, Th=25 mm |  |  | 5 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=22 mm, Th=25 mm |  |  | 41 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=28 mm, Th=40 mm |  |  | 12 | m
| PE foam lagging, λ(20°C)=0,038W/mK | In.diam.=35 mm, Th=40 mm |  |  | 5 | m
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 |  |  |  | - 26 -

## List of pipes, pipe fitting-2
Project: Example of radiant heating installation with radiant ceiling steel panels
List of valves and fittings
Product |  | Size | Catalogue code |  | Qty. | Unit
Neutral valves cataloge - typical construction
Valves
| Ball valve. FT | 15, kvs=13.0 | DN15 |  | 10 | pcs.
| Regulatory automatic balancing valve, FT | 15 | DN15 |  | 10 | pcs.
Heads (thermostatic)/Actuators
| Actuator |  | Act. |  | 10 | pcs.
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 |  |  |  | - 27 -

## List of pipes, pipe fitting-3
Project: Example of radiant heating installation with radiant ceiling steel panels
List of panel system components
Product |  | Length | Height/Width | Depth/Thickness | Catalogue code |  | Qty. | Unit
Neutral ceiling and wall panels
Panels
| Ceiling steel panel Type-1 (0,32m) | 6000 | 320 | 55 |  |  | 2 | pcs.
| Ceiling steel panel Type-1 (0,32m) | 14000 | 320 | 55 |  |  | 8 | pcs.
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [5 empty] | - 28 -

## Pipes summary
Project: Example of radiant heating installation with radiant ceiling steel panels
Pipes summary
Product | Size | Catalogue code | Insulated | Non-insulated | User specified | Sized | Under design |  | Existing | From radiant systems
|  |  | m | m | m | m | m |  | m | m
Hard copper pipe, Type X bars | 28 x 1,5 |  | 11,83 |  |  | 11,83 | 11,83
Hard copper pipe, Type X bars | 35 x 1,5 |  | 4,87 |  |  | 4,87 | 4,87
Soft copper pipe, Type X coils | 12 x 1 |  | 2,35 |  |  | 2,35 | 2,35
Soft copper pipe, Type X coils | 15 x 1 |  | 15,84 |  |  | 15,84 | 15,84
Soft copper pipe, Type X coils | 18 x 1 |  | 4,88 |  |  | 4,88 | 4,88
Soft copper pipe, Type X coils | 22 x 1 |  | 40,69 |  |  | 40,69 | 40,69
InstalSystem 5 EN (BETA) (Rev. 0.0.B33) © InstalSoft 1996-2016 | [7 empty] | - 29 -