## General results heating
Project:
General results heating
No. of sources |  |  |  | 1
Total number of terminal units |  |  |  | 78
Total number of pipe-runs |  |  |  | 210
Total number of manifolds |  |  |  | 8
Total number of pumps |  |  |  | 9
Total number of flat stations |  |  |  | 8
Spec. total rooms heat loss ΦH |  |  |  | 26567 |  | W
Spec. total required output of other TU's |  |  |  | 0 |  | W
Total declared output of receptors Φreq |  |  |  | 26567 |  | W
Calculation standards:
Radiators sizing standard |  |  |  | EN 442-2
Floor heating standard |  |  |  | EN 1264: 1:2011 2:2013 3,4:2009 5:2008
Wall and ceiling panels calculation standard |  |  |  | EN 14037
Flat stations (sizing diameters of the distribution installation pipes) |  |  |  | TU Dresden
Source: Other (vert.): 1, Application: Heating systems, Medium: Water
| Source elevation |  |  | -1,6 |  | m
| Supply and return temperature |  |  | 75,0 / 20,9 |  | °C
| Total output |  |  | 163413 |  | W
| Total output of convectors Φconv,H |  |  | 4494 |  | W
| Total output of radiant heaters Φrh,H |  |  | 21224 |  | W
| Total output of other terminal units |  |  | 0 |  | W
| Heat gains from pipe-runs accounted for in balance |  |  | 0 |  | W
| Not utilized heat loss of pipe-runs |  |  | 1617 |  | W
| Losses of radiant systems to outside of source feed area |  |  | 5430 |  | W
| Losses of radiant systems within source feed area |  |  | 2264 |  | W
| Available pressure |  |  | 35,3 |  | kPa
| Pressure drop along critical route |  |  | 48,4 |  | kPa
| Pressure drop on critical terminal unit |  |  | 25,0 |  | kPa
| Press. drop on source |  |  | 0,0 |  | kPa
| Flow rate in source |  |  | 2624,3 |  | kg/h
| Critical receptor: |  | 104-1
| Critical TU route length |  |  | 23,5 |  | m
| Pump table: | (no name)
| Flow rate |  |  | 2624,3 |  | kg/h
| Pressure |  |  | 12,3 |  | kPa
| Pump table: | Pump_PumpUnit
| Flow rate |  |  | 537,9 |  | kg/h
| Pressure |  |  | 20,6 |  | kPa
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 |  |  |  |  | - 1 -
Project:
| Pump table: | Pump_PumpUnit
| Flow rate |  |  | 408,9 |  | kg/h
| Pressure |  |  | 12,6 |  | kPa
| Pump table: | Pump_PumpUnit
| Flow rate |  |  | 393,0 |  | kg/h
| Pressure |  |  | 8,2 |  | kPa
| Pump table: | Pump_PumpUnit
| Flow rate |  |  | 337,8 |  | kg/h
| Pressure |  |  | 26,7 |  | kPa
| Pump table: | Pump_PumpUnit
| Flow rate |  |  | 329,9 |  | kg/h
| Pressure |  |  | 7,1 |  | kPa
| Pump table: | Pump_PumpUnit
| Flow rate |  |  | 327,4 |  | kg/h
| Pressure |  |  | 22,8 |  | kPa
| Pump table: | Pump_PumpUnit
| Flow rate |  |  | 272,1 |  | kg/h
| Pressure |  |  | 14,0 |  | kPa
| Pump table: | Pump_PumpUnit
| Flow rate |  |  | 264,6 |  | kg/h
| Pressure |  |  | 12,0 |  | kPa
| Capacity of system incl. terminal units |  |  | 438,44 |  | dm³
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 |  |  |  |  | - 2 -

## Heating terminal units
Project:
Heating terminal units
Terminal unit symbol |  |  |  | Room symbol |  |  | Room temperature | Specified terminal unit output | Sized terminal unit output | Mass flow rate | Supply temperature | Return temperature | Type |  | Length |  | Height / Width |  |  | Depth / Thickness |  | Terminal unit oversizing or undersizing percentage
Terminal unit |  |  |  | Room |  |  | θi,H | Φreq,H | ΦH | m | θs,H | θr,H | Type |  | L |  | H/W |  |  | D |  | A'/A
[7 empty] | °C | W | W | kg/h | °C | °C |  |  | mm |  | mm |  |  | mm |  | %
Storey: |  | 1 | Building unit: |  |  | 02
| 101-1 |  |  | 101 |  |  | 20,0 | 216 | 350 | 18,6 | 73,7 | 57,5 | PLV11_600 |  | 400 |  | 600 |  |  | 60 |  | 162
| 103-1 |  |  | 103 |  |  | 20,0 | 134 | 255 | 11,5 | 73,2 | 54,2 | PLV11_450 |  | 400 |  | 450 |  |  | 60 |  | 190
| 104-1 |  |  | 104 |  |  | 20,0 | 216 | 350 | 18,6 | 73,7 | 57,5 | PLV11_600 |  | 400 |  | 600 |  |  | 60 |  | 162
| 106-1 |  |  | 106 |  |  | 20,0 | 134 | 256 | 11,5 | 73,3 | 54,3 | PLV11_450 |  | 400 |  | 450 |  |  | 60 |  | 191
| 109-1 |  |  | 109 |  |  | 24,0 | 85 | 203 | 8,6 | 71,9 | 51,6 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 238
| 111-1 |  |  | 111 |  |  | 24,0 | 80 | 202 | 8,6 | 71,8 | 51,6 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 252
| 112-1 |  |  | 112 |  |  | 24,0 | 80 | 197 | 8,6 | 70,7 | 51,0 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 246
| 115-1 |  |  | 115 |  |  | 24,0 | 139 | 217 | 11,9 | 71,3 | 55,7 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 156
| 116-1 |  |  | 116 |  |  | 24,0 | 139 | 219 | 11,9 | 71,7 | 55,9 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 158
| Terminal unit symbol |  |  |  | Room symbol |  |  | Type |  |  |  | Diameter |  | Pressure drop |  | Xp |  | A |  |  | Setting
[12 empty] | mm |  | kPa
| 101-1 |  |  |  | 101 |  |  | VK radiator insert |  |  |  | 0 |  | 10,81 |  | 2,0 |  | 0,60 |  |  | 3,00
| 101-1 |  |  |  | 101 |  |  | Valve connection, straight MT (2-p) 15 |  |  |  | 15 |  | 0,29 |  | 0,0 |  | 0,00 |  |  | kv= 0,35
| 103-1 |  |  |  | 103 |  |  | VK radiator insert |  |  |  | 0 |  | 12,12 |  | 2,0 |  | 0,70 |  |  | 2,00
| 103-1 |  |  |  | 103 |  |  | Valve connection, straight MT (2-p) 15 |  |  |  | 15 |  | 0,11 |  | 0,0 |  | 0,00 |  |  | kv= 0,35
| 104-1 |  |  |  | 104 |  |  | VK radiator insert |  |  |  | 0 |  | 24,38 |  | 2,0 |  | 0,65 |  |  | 2,00
| 104-1 |  |  |  | 104 |  |  | Valve connection, straight MT (2-p) 15 |  |  |  | 15 |  | 0,58 |  | 0,0 |  | 0,00 |  |  | kv= 0,25
| 106-1 |  |  |  | 106 |  |  | VK radiator insert |  |  |  | 0 |  | 12,07 |  | 2,0 |  | 0,70 |  |  | 2,00
| 106-1 |  |  |  | 106 |  |  | Valve connection, straight MT (2-p) 15 |  |  |  | 15 |  | 0,11 |  | 0,0 |  | 0,00 |  |  | kv= 0,35
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [18 empty] | - 3 -
Project:
Terminal unit |  |  |  | Room |  |  | θi,H | Φreq,H | ΦH | m | θs,H | θr,H | Type |  | L |  | H/W |  |  | D |  | A'/A
[7 empty] | °C | W | W | kg/h | °C | °C |  |  | mm |  | mm |  |  | mm |  | %
| 109-1 |  |  |  | 109 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 25,12 |  | 2,0 |  | 0,67 |  |  | 1,00
| 111-1 |  |  |  | 111 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 25,09 |  | 2,0 |  | 0,67 |  |  | 1,00
| 112-1 |  |  |  | 112 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 11,23 |  | 2,0 |  | 0,62 |  |  | 1,00
| 115-1 |  |  |  | 115 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 12,32 |  | 2,0 |  | 0,72 |  |  | 2,00
| 116-1 |  |  |  | 116 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 12,27 |  | 2,0 |  | 0,72 |  |  | 2,00
Storey: |  | 2 | Building unit: |  |  | 08
| 201-1 |  |  | 201 |  |  | 20,0 | 216 | 349 | 18,6 | 73,6 | 57,4 | PLV11_600 |  | 400 |  | 600 |  |  | 60 |  | 161
| 203-1 |  |  | 203 |  |  | 20,0 | 134 | 254 | 11,5 | 73,1 | 54,1 | PLV11_450 |  | 400 |  | 450 |  |  | 60 |  | 189
| 204-1 |  |  | 204 |  |  | 20,0 | 216 | 350 | 18,6 | 73,6 | 57,5 | PLV11_600 |  | 400 |  | 600 |  |  | 60 |  | 162
| 206-1 |  |  | 206 |  |  | 20,0 | 134 | 255 | 11,5 | 73,2 | 54,2 | PLV11_450 |  | 400 |  | 450 |  |  | 60 |  | 190
| 209-1 |  |  | 209 |  |  | 24,0 | 85 | 202 | 8,6 | 71,9 | 51,6 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 238
| 211-1 |  |  | 211 |  |  | 24,0 | 80 | 202 | 8,6 | 71,8 | 51,6 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 252
| 212-1 |  |  | 212 |  |  | 24,0 | 80 | 196 | 8,6 | 70,6 | 51,0 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 245
| 215-1 |  |  | 215 |  |  | 24,0 | 139 | 217 | 11,9 | 71,2 | 55,6 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 156
| 216-1 |  |  | 216 |  |  | 24,0 | 139 | 219 | 11,9 | 71,6 | 55,8 | BTHV_550_135 |  | 550 |  | 420 |  |  | 135 |  | 157
| Terminal unit symbol |  |  |  | Room symbol |  |  | Type |  |  |  | Diameter |  | Pressure drop |  | Xp |  | A |  |  | Setting
[12 empty] | mm |  | kPa
| 201-1 |  |  |  | 201 |  |  | VK radiator insert |  |  |  | 0 |  | 3,07 |  | 2,0 |  | 0,40 |  |  | 4,00
| 201-1 |  |  |  | 201 |  |  | Valve connection, straight MT (2-p) 15 |  |  |  | 15 |  | 0,14 |  | 0,0 |  | 0,00 |  |  | kv= 0,50
| 203-1 |  |  |  | 203 |  |  | VK radiator insert |  |  |  | 0 |  | 6,42 |  | 2,0 |  | 0,63 |  |  | 2,00
| 203-1 |  |  |  | 203 |  |  | Valve connection, straight MT (2-p) 15 |  |  |  | 15 |  | 0,09 |  | 0,0 |  | 0,00 |  |  | kv= 0,40
| 204-1 |  |  |  | 204 |  |  | VK radiator insert |  |  |  | 0 |  | 17,33 |  | 2,0 |  | 0,59 |  |  | 2,00
| 204-1 |  |  |  | 204 |  |  | Valve connection, straight MT (2-p) 15 |  |  |  | 15 |  | 0,40 |  | 0,0 |  | 0,00 |  |  | kv= 0,30
| 206-1 |  |  |  | 206 |  |  | VK radiator insert |  |  |  | 0 |  | 6,40 |  | 2,0 |  | 0,63 |  |  | 2,00
| 206-1 |  |  |  | 206 |  |  | Valve connection, straight MT (2-p) 15 |  |  |  | 15 |  | 0,09 |  | 0,0 |  | 0,00 |  |  | kv= 0,40
| 209-1 |  |  |  | 209 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 17,90 |  | 2,0 |  | 0,61 |  |  | 1,00
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [18 empty] | - 4 -
Project:
Terminal unit |  |  |  | Room |  |  | θi,H | Φreq,H | ΦH | m | θs,H | θr,H | Type |  | L |  | H/W |  |  | D |  | A'/A
[7 empty] | °C | W | W | kg/h | °C | °C |  |  | mm |  | mm |  |  | mm |  | %
| 211-1 |  |  |  | 211 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 17,86 |  | 2,0 |  | 0,61 |  |  | 1,00
| 212-1 |  |  |  | 212 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 3,33 |  | 2,0 |  | 0,44 |  |  | 2,00
| 215-1 |  |  |  | 215 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 6,59 |  | 2,0 |  | 0,65 |  |  | 2,00
| 216-1 |  |  |  | 216 |  |  | Set for bathroom radiators - angle |  |  |  | 0 |  | 6,57 |  | 2,0 |  | 0,64 |  |  | 2,00
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [18 empty] | - 5 -

## Heating pipe-runs
Project:
Heating pipe-runs
Pipe-run type |  | Pipe-run no. |  | Connection piperun No. | Heat quantity carried by pipe-run | Diameter | Length | Specific friction resistance | Total friction loss | Total pressure loss | Flow velocity | Mass flow rate | Insulation thickness |  | Inlet temperature | Specific heat loss in pipe-run
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. |  | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm |  | °C | W/m
Source: |  |  | 1
| S | 1 |  | Source: 1 | 164753 | 50 x 4,5 | 0,23 | 76 | 2,9 | 472 | 0,57 | 2624,3 | 50 |  | 75,0 | 12,25
| R | 1 |  | Source: 1 | 164750 | 50 x 4,5 | 0,33 | 92 | 4,1 | 656 | 0,55 | 2624,3 | 50 |  | 20,9 | 0,20
| S | 1_A |  | 1 | 164750 | 50 x 4,5 | 2,53 | 76 | 2,1 | 522 | 0,57 | 2624,3 | 50 |  | 75,0 | 12,25
| R | 1_A |  | 1 | 164750 | 50 x 4,5 | 2,27 | 92 | 2,1 | 530 | 0,55 | 2624,3 | 50 |  | 20,9 | 0,20
| S | 2 |  | 1_A | 125364 | 40 x 4,0 | 2,38 | 143 | 2,6 | 749 | 0,68 | 1922,2 | 40 |  | 75,0 | 12,06
| R | 2 |  | 1_A | 125364 | 40 x 4,0 | 2,33 | 176 | 2,6 | 807 | 0,66 | 1922,2 | 40 |  | 18,7 | -0,26
| S | 3 |  | 2 | 57193 | 32 x 3,0 | 4,08 | 91 | 5,2 | 1221 | 0,46 | 848,6 | 40 |  | 75,0 | 10,66
| R | 3 |  | 2 | 57148 | 32 x 3,0 | 3,92 | 113 | 5,2 | 1273 | 0,44 | 848,6 | 40 |  | 16,8 | -0,60
| S | 3_A |  | 3 | 57150 | 32 x 3,0 | 0,39 | 91 | 0,0 | 35 | 0,46 | 848,6 | 40 |  | 74,9 | 10,65
| R | 3_A |  | 3 | 57150 | 32 x 3,0 | 0,39 | 113 | 0,0 | 44 | 0,44 | 848,6 | 40 |  | 16,8 | -0,60
| S | 4 |  | 3_A | 33332 | 25 x 2,5 | 0,96 | 125 | 3,9 | 514 | 0,45 | 500,8 | 25 |  | 74,9 | 10,63
| R | 4 |  | 3_A | 33322 | 25 x 2,5 | 0,96 | 156 | 3,9 | 533 | 0,44 | 500,8 | 25 |  | 17,5 | -0,41
| S | 5 |  | FS | 581 | 16 x 2,0 | 0,80 | 5 | 0,8 | 5 | 0,06 | 23,5 | 25 |  | 74,9 | 8,42
| R | 5 |  | FS | 581 | 16 x 2,0 | 0,84 | 7 | 0,4 | 6 | 0,06 | 23,5 | 25 |  | 53,7 | 6,11
| S | 6 |  | 5 | 284 | 16 x 2,0 | 2,13 | 2 | 5,5 | 13 | 0,03 | 11,5 | 25 |  | 74,7 | 8,30
| R | 6 |  | 5 | 286 | 16 x 2,0 | 5,05 | 3 | 5,1 | 24 | 0,03 | 11,9 | 25 |  | 55,9 | 6,69
| S | 7 |  | 5 | 286 | 16 x 2,0 | 5,11 | 3 | 5,1 | 20 | 0,03 | 11,9 | 25 |  | 74,7 | 8,16
| R | 7 |  | 5 | 284 | 16 x 2,0 | 2,23 | 3 | 5,1 | 14 | 0,03 | 11,5 | 25 |  | 54,3 | 6,79
| S | 8 |  | 3_A | 23818 | 25 x 2,5 | 3,30 | 66 | 4,0 | 484 | 0,32 | 347,8 | 25 |  | 74,9 | 11,60
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [13 empty] | - 6 -
Project:
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. |  | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm |  | °C | W/m
| R | 8 |  | 3_A | 23766 | 25 x 2,5 | 3,30 | 83 | 4,0 | 535 | 0,31 | 347,8 | 25 |  | 15,9 | -0,85
| S | 8_A |  | 8 | 23780 | 25 x 2,5 | 0,96 | 66 | 0,8 | 102 | 0,32 | 347,8 | 25 |  | 74,8 | 10,61
| R | 8_A |  | 8 | 23769 | 25 x 2,5 | 0,96 | 83 | 0,8 | 118 | 0,31 | 347,8 | 25 |  | 15,9 | -0,70
| S | 9 |  | FS | 580 | 16 x 2,0 | 0,80 | 5 | 0,8 | 5 | 0,06 | 23,5 | 25 |  | 74,8 | 8,41
| R | 9 |  | FS | 580 | 16 x 2,0 | 0,84 | 7 | 0,4 | 6 | 0,06 | 23,5 | 25 |  | 53,6 | 6,11
| S | 10 |  | 9 | 283 | 16 x 2,0 | 2,13 | 2 | 5,5 | 13 | 0,03 | 11,5 | 25 |  | 74,6 | 8,28
| R | 10 |  | 9 | 286 | 16 x 2,0 | 5,05 | 3 | 5,1 | 24 | 0,03 | 11,9 | 25 |  | 55,8 | 6,69
| S | 11 |  | 9 | 286 | 16 x 2,0 | 5,11 | 3 | 5,1 | 20 | 0,03 | 11,9 | 25 |  | 74,6 | 8,15
| R | 11 |  | 9 | 283 | 16 x 2,0 | 2,23 | 3 | 5,1 | 14 | 0,03 | 11,5 | 25 |  | 54,2 | 6,79
| S | 12 |  | 2 | 88594 | 40 x 4,0 | 9,36 | 77 | 1,4 | 1036 | 0,48 | 1353,5 | 40 |  | 75,0 | 12,05
| R | 12 |  | 2 | 88594 | 40 x 4,0 | 9,25 | 95 | 1,4 | 1187 | 0,47 | 1353,5 | 40 |  | 18,5 | -0,30
| S | 13 |  | 12 | 69983 | 32 x 3,0 | 0,58 | 120 | 5,2 | 722 | 0,53 | 994,6 | 40 |  | 74,9 | 10,65
| R | 13 |  | 12 | 69976 | 32 x 3,0 | 0,74 | 152 | 5,2 | 748 | 0,52 | 994,6 | 40 |  | 14,2 | -1,10
| S | 13_A |  | 13 | 69977 | 32 x 3,0 | 0,39 | 120 | 0,0 | 47 | 0,53 | 994,6 | 40 |  | 74,9 | 10,65
| R | 13_A |  | 13 | 69977 | 32 x 3,0 | 0,39 | 152 | 0,0 | 60 | 0,52 | 994,6 | 40 |  | 14,2 | -1,10
| S | 14 |  | 13_A | 45572 | 32 x 3,0 | 0,96 | 57 | 6,0 | 622 | 0,35 | 655,6 | 40 |  | 74,9 | 9,92
| R | 14 |  | 13_A | 45561 | 32 x 3,0 | 0,96 | 73 | 6,0 | 621 | 0,34 | 655,6 | 40 |  | 14,9 | -0,84
| S | 15 |  | FS | 649 | 16 x 2,0 | 0,78 | 6 | 4,1 | 14 | 0,07 | 27,2 | 25 |  | 74,9 | 8,42
| R | 15 |  | FS | 647 | 16 x 2,0 | 0,82 | 8 | 4,1 | 16 | 0,07 | 27,2 | 25 |  | 54,3 | 6,20
| S | 15_A |  | 15 | 643 | 16 x 2,0 | 1,48 | 6 | 0,0 | 9 | 0,07 | 27,2 | 25 |  | 74,7 | 8,37
| R | 15_A |  | 15 | 643 | 16 x 2,0 | 1,49 | 8 | 0,0 | 11 | 0,07 | 27,2 | 25 |  | 54,5 | 6,31
| S | 16 |  | 15_A | 371 | 16 x 2,0 | 1,55 | 4 | 5,2 | 17 | 0,05 | 18,6 | 25 |  | 74,3 | 8,30
| R | 16 |  | 15_A | 371 | 16 x 2,0 | 1,70 | 5 | 5,2 | 19 | 0,05 | 18,6 | 25 |  | 57,5 | 6,84
| S | 17 |  | 15_A | 252 | 16 x 2,0 | 1,27 | 2 | 4,7 | 5 | 0,02 | 8,6 | 25 |  | 74,3 | 8,26
| R | 17 |  | 15_A | 241 | 16 x 2,0 | 4,45 | 3 | 2,6 | 14 | 0,02 | 8,6 | 25 |  | 51,0 | 6,65
| S | 17_A |  | 17 | 241 | 16 x 2,0 | 3,14 | 2 | 1,2 | 6 | 0,02 | 8,6 | 25 |  | 73,2 | 7,98
| S | 18 |  | 13_A | 24408 | 25 x 2,5 | 3,30 | 63 | 4,3 | 470 | 0,31 | 339,0 | 25 |  | 74,9 | 11,59
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [13 empty] | - 7 -
Project:
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. |  | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm |  | °C | W/m
| R | 18 |  | 13_A | 24354 | 25 x 2,5 | 3,30 | 81 | 4,3 | 524 | 0,30 | 339,0 | 25 |  | 12,8 | -1,48
| S | 18_A |  | 18 | 24370 | 25 x 2,5 | 0,96 | 63 | 0,8 | 97 | 0,31 | 339,0 | 25 |  | 74,8 | 10,61
| R | 18_A |  | 18 | 24359 | 25 x 2,5 | 0,96 | 81 | 0,8 | 114 | 0,30 | 339,0 | 25 |  | 12,8 | -1,27
| S | 19 |  | FS | 648 | 16 x 2,0 | 0,78 | 6 | 4,1 | 14 | 0,07 | 27,2 | 25 |  | 74,8 | 8,40
| R | 19 |  | FS | 646 | 16 x 2,0 | 0,82 | 8 | 4,1 | 16 | 0,07 | 27,2 | 25 |  | 54,2 | 6,20
| S | 19_A |  | 19 | 641 | 16 x 2,0 | 1,48 | 6 | 0,0 | 9 | 0,07 | 27,2 | 25 |  | 74,6 | 8,36
| R | 19_A |  | 19 | 641 | 16 x 2,0 | 1,49 | 8 | 0,0 | 11 | 0,07 | 27,2 | 25 |  | 54,5 | 6,31
| S | 20 |  | 19_A | 370 | 16 x 2,0 | 1,55 | 4 | 5,2 | 17 | 0,05 | 18,6 | 25 |  | 74,2 | 8,28
| R | 20 |  | 19_A | 370 | 16 x 2,0 | 1,70 | 5 | 5,2 | 19 | 0,05 | 18,6 | 25 |  | 57,4 | 6,84
| S | 21 |  | 19_A | 251 | 16 x 2,0 | 1,27 | 2 | 4,7 | 5 | 0,02 | 8,6 | 25 |  | 74,2 | 8,24
| R | 21 |  | 19_A | 241 | 16 x 2,0 | 4,45 | 3 | 2,6 | 14 | 0,02 | 8,6 | 25 |  | 51,0 | 6,65
| S | 21_A |  | 21 | 241 | 16 x 2,0 | 3,14 | 2 | 1,2 | 6 | 0,02 | 8,6 | 25 |  | 73,1 | 7,96
| S | 22 |  | 12 | 57231 | 32 x 3,0 | 0,06 | 91 | 4,0 | 427 | 0,46 | 850,3 | 40 |  | 74,9 | 10,65
| R | 22 |  | 12 | 57185 | 32 x 3,0 | 0,17 | 114 | 4,0 | 429 | 0,44 | 850,3 | 40 |  | 16,9 | -0,59
| S | 22_A |  | 22 | 57230 | 32 x 3,0 | 4,08 | 91 | 2,6 | 635 | 0,46 | 850,3 | 40 |  | 74,9 | 10,64
| R | 22_A |  | 22 | 57185 | 32 x 3,0 | 3,92 | 114 | 2,6 | 703 | 0,44 | 850,3 | 40 |  | 16,9 | -0,60
| S | 22_B |  | 22_A | 57187 | 32 x 3,0 | 0,39 | 91 | 0,0 | 36 | 0,46 | 850,3 | 40 |  | 74,9 | 10,64
| R | 22_B |  | 22_A | 57187 | 32 x 3,0 | 0,39 | 114 | 0,0 | 44 | 0,44 | 850,3 | 40 |  | 16,9 | -0,60
| S | 23 |  | 22_B | 33353 | 25 x 2,5 | 0,96 | 125 | 3,9 | 515 | 0,46 | 501,8 | 25 |  | 74,9 | 10,62
| R | 23 |  | 22_B | 33343 | 25 x 2,5 | 0,96 | 156 | 3,9 | 535 | 0,44 | 501,8 | 25 |  | 17,5 | -0,41
| S | 24 |  | FS | 586 | 16 x 2,0 | 0,84 | 5 | 0,4 | 5 | 0,06 | 23,5 | 25 |  | 74,8 | 8,41
| R | 24 |  | FS | 586 | 16 x 2,0 | 0,80 | 7 | 0,8 | 7 | 0,06 | 23,5 | 25 |  | 53,5 | 6,07
| S | 25 |  | 24 | 283 | 16 x 2,0 | 2,27 | 2 | 5,1 | 13 | 0,03 | 11,5 | 25 |  | 74,6 | 8,28
| R | 25 |  | 24 | 291 | 16 x 2,0 | 5,69 | 3 | 5,1 | 26 | 0,03 | 11,9 | 25 |  | 55,7 | 6,66
| S | 26 |  | 24 | 291 | 16 x 2,0 | 5,58 | 3 | 5,1 | 21 | 0,03 | 11,9 | 25 |  | 74,6 | 8,13
| R | 26 |  | 24 | 283 | 16 x 2,0 | 2,11 | 3 | 5,5 | 14 | 0,03 | 11,5 | 25 |  | 54,2 | 6,80
| S | 27 |  | 22_B | 23834 | 25 x 2,5 | 3,30 | 66 | 4,0 | 486 | 0,32 | 348,5 | 25 |  | 74,9 | 11,59
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [13 empty] | - 8 -
Project:
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. |  | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm |  | °C | W/m
| R | 27 |  | 22_B | 23782 | 25 x 2,5 | 3,30 | 84 | 4,0 | 537 | 0,31 | 348,5 | 25 |  | 15,9 | -0,85
| S | 27_A |  | 27 | 23796 | 25 x 2,5 | 0,96 | 66 | 0,8 | 102 | 0,32 | 348,5 | 25 |  | 74,8 | 10,60
| R | 27_A |  | 27 | 23785 | 25 x 2,5 | 0,96 | 84 | 0,8 | 118 | 0,31 | 348,5 | 25 |  | 15,9 | -0,70
| S | 28 |  | FS | 584 | 16 x 2,0 | 0,84 | 5 | 0,4 | 5 | 0,06 | 23,5 | 25 |  | 74,7 | 8,39
| R | 28 |  | FS | 584 | 16 x 2,0 | 0,80 | 7 | 0,8 | 7 | 0,06 | 23,5 | 25 |  | 53,4 | 6,07
| S | 29 |  | 28 | 283 | 16 x 2,0 | 2,27 | 2 | 5,1 | 13 | 0,03 | 11,5 | 25 |  | 74,5 | 8,26
| R | 29 |  | 28 | 291 | 16 x 2,0 | 5,69 | 3 | 5,1 | 26 | 0,03 | 11,9 | 25 |  | 55,6 | 6,66
| S | 30 |  | 28 | 291 | 16 x 2,0 | 5,58 | 3 | 5,1 | 21 | 0,03 | 11,9 | 25 |  | 74,5 | 8,11
| R | 30 |  | 28 | 283 | 16 x 2,0 | 2,11 | 3 | 5,5 | 14 | 0,03 | 11,5 | 25 |  | 54,1 | 6,80
| S | 31 |  | 1_A | 97957 | 40 x 4,0 | 0,45 | 97 | 4,4 | 700 | 0,55 | 1543,0 | 40 |  | 75,0 | 12,06
| R | 31 |  | 1_A | 97949 | 40 x 4,0 | 0,56 | 118 | 4,4 | 706 | 0,53 | 1543,0 | 40 |  | 20,2 | 0,05
| S | 31_A |  | 31 | 97951 | 40 x 4,0 | 0,22 | 97 | 2,1 | 328 | 0,55 | 1543,0 | 40 |  | 75,0 | 12,06
| R | 31_A |  | 31 | 97949 | 40 x 4,0 | 0,32 | 118 | 2,1 | 336 | 0,53 | 1543,0 | 40 |  | 20,2 | 0,05
| S | 31_B |  | 31_A | 97949 | 40 x 4,0 | 0,39 | 97 | 0,0 | 38 | 0,55 | 1543,0 | 40 |  | 75,0 | 12,06
| R | 31_B |  | 31_A | 97949 | 40 x 4,0 | 0,39 | 118 | 0,0 | 46 | 0,53 | 1543,0 | 40 |  | 20,2 | 0,05
| S | 32 |  | 31_B | 51783 | 32 x 3,0 | 3,71 | 86 | 8,6 | 1268 | 0,44 | 822,8 | 40 |  | 75,0 | 9,93
| R | 32 |  | 31_B | 51747 | 32 x 3,0 | 3,71 | 105 | 8,6 | 1315 | 0,43 | 822,8 | 40 |  | 20,7 | 0,10
| S | 33 |  | FS | 893 | 16 x 2,0 | 0,82 | 14 | 0,4 | 13 | 0,09 | 35,8 | 25 |  | 74,9 | 8,43
| R | 33 |  | FS | 893 | 16 x 2,0 | 0,79 | 10 | 0,4 | 10 | 0,09 | 35,8 | 25 |  | 53,5 | 6,21
| S | 34 |  | 33 | 636 | 16 x 2,0 | 1,64 | 6 | 3,9 | 25 | 0,07 | 27,2 | 25 |  | 74,8 | 8,39
| R | 34 |  | 33 | 636 | 16 x 2,0 | 1,75 | 8 | 3,9 | 29 | 0,07 | 27,2 | 25 |  | 54,9 | 6,43
| S | 35 |  | 34 | 372 | 16 x 2,0 | 1,70 | 4 | 5,2 | 18 | 0,05 | 18,6 | 25 |  | 74,3 | 8,30
| R | 35 |  | 34 | 372 | 16 x 2,0 | 1,67 | 5 | 5,2 | 19 | 0,05 | 18,6 | 25 |  | 57,5 | 6,84
| S | 36 |  | 34 | 240 | 16 x 2,0 | 3,10 | 2 | 2,6 | 8 | 0,02 | 8,6 | 25 |  | 74,3 | 8,15
| R | 36 |  | 34 | 240 | 16 x 2,0 | 2,97 | 3 | 2,6 | 10 | 0,02 | 8,6 | 25 |  | 51,6 | 6,72
| S | 37 |  | 33 | 247 | 16 x 2,0 | 3,52 | 2 | 5,5 | 22 | 0,02 | 8,6 | 25 |  | 74,8 | 8,19
| R | 37 |  | 33 | 247 | 16 x 2,0 | 3,52 | 3 | 5,5 | 25 | 0,02 | 8,6 | 25 |  | 51,6 | 6,69
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [13 empty] | - 9 -
Project:
Type |  | Pipe-run symbol |  | Symbol of conn. pipes | ΦH | Diam. | L | R | ζ | Tot. press. drop | v | m | Insul. |  | θinlet,H | qH
[5 empty] | W | mm | m | Pa/m |  | Pa | m/s | kg/h | mm |  | °C | W/m
| S | 38 |  | 31_B | 46160 | 32 x 3,0 | 3,30 | 68 | 4,0 | 617 | 0,39 | 720,3 | 40 |  | 75,0 | 10,66
| R | 38 |  | 31_B | 46088 | 32 x 3,0 | 3,30 | 84 | 4,0 | 659 | 0,38 | 720,3 | 40 |  | 19,7 | -0,06
| S | 38_A |  | 38 | 46125 | 32 x 3,0 | 3,71 | 68 | 6,0 | 689 | 0,39 | 720,3 | 40 |  | 74,9 | 9,93
| R | 38_A |  | 38 | 46089 | 32 x 3,0 | 3,71 | 84 | 6,0 | 736 | 0,38 | 720,3 | 40 |  | 19,7 | -0,04
| S | 39 |  | FS | 892 | 16 x 2,0 | 0,82 | 14 | 0,4 | 13 | 0,09 | 35,8 | 25 |  | 74,9 | 8,43
| R | 39 |  | FS | 892 | 16 x 2,0 | 0,79 | 10 | 0,4 | 10 | 0,09 | 35,8 | 25 |  | 53,5 | 6,21
| S | 40 |  | 39 | 635 | 16 x 2,0 | 1,64 | 6 | 3,9 | 25 | 0,07 | 27,2 | 25 |  | 74,7 | 8,38
| R | 40 |  | 39 | 635 | 16 x 2,0 | 1,75 | 8 | 3,9 | 29 | 0,07 | 27,2 | 25 |  | 54,9 | 6,43
| S | 41 |  | 40 | 372 | 16 x 2,0 | 1,70 | 4 | 5,2 | 18 | 0,05 | 18,6 | 25 |  | 74,3 | 8,29
| R | 41 |  | 40 | 372 | 16 x 2,0 | 1,67 | 5 | 5,2 | 19 | 0,05 | 18,6 | 25 |  | 57,5 | 6,84
| S | 42 |  | 40 | 240 | 16 x 2,0 | 3,10 | 2 | 2,6 | 8 | 0,02 | 8,6 | 25 |  | 74,3 | 8,14
| R | 42 |  | 40 | 240 | 16 x 2,0 | 2,97 | 3 | 2,6 | 10 | 0,02 | 8,6 | 25 |  | 51,6 | 6,72
| S | 43 |  | 39 | 246 | 16 x 2,0 | 3,52 | 2 | 5,5 | 22 | 0,02 | 8,6 | 25 |  | 74,7 | 8,18
| R | 43 |  | 39 | 246 | 16 x 2,0 | 3,52 | 3 | 5,5 | 25 | 0,02 | 8,6 | 25 |  | 51,6 | 6,69
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [13 empty] | - 10 -

## Components on pipe-runs
Project:
Components on pipe-runs
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 1, Source: 1, m= 2624,3 kg/h, Diameter: 50 x 4,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 54 mm. Thickness = 50 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 50 - 50 |  | 2,1 |  |  | 329
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 50 - 1½"MT |  | 0,4 |  |  | 63
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 1¾"FT - 1½"FT |  | 0,4 |  |  | 63
Pipe-run (R) 1, Source: 1, m= 2624,3 kg/h, Diameter: 50 x 4,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 54 mm. Thickness = 50 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 50 - 50 |  | 2,1 |  |  | 320
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 50 - 1½"MT |  | 0,4 |  |  | 61
| Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 1¾"FT - 1½"FT |  | 0,4 |  |  | 61
| NONE | Pump |  |  |  |  | -12323
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 50 - 1½"MT |  | 0,4 |  |  | 61
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 50 - 1½"MT |  | 0,4 |  |  | 61
| Brass and steel pipe couplings and fittings | Female connector, straight, imperial 1½"FT - 1½"FT |  | 0,4 |  |  | 61
Pipe-run (S) 1_A, Source: 1, m= 2624,3 kg/h, Diameter: 50 x 4,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 54 mm. Thickness = 50 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 50 - 40 - 50 |  |  |  |  | 0
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 50 - 50 |  | 2,1 |  |  | 329
Pipe-run (R) 1_A, Source: 1, m= 2624,3 kg/h, Diameter: 50 x 4,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 54 mm. Thickness = 50 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 50 - 40 - 50 |  |  |  |  | 0
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 50 - 50 |  | 2,1 |  |  | 320
Pipe-run (S) 10, Source: 1, m= 11,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 11 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 10, Source: 1, m= 11,9 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 11, Source: 1, m= 11,9 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 11, Source: 1, m= 11,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 12, Source: 1, m= 1353,5 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 40 |  | 1,4 |  |  | 317
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  |  |  |  | 0
Pipe-run (R) 12, Source: 1, m= 1353,5 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 40 |  | 1,4 |  |  | 308
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 12 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  |  |  |  | 0
Pipe-run (S) 13, Source: 1, m= 994,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  | 2,6 |  |  | 292
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 361
Pipe-run (R) 13, Source: 1, m= 994,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  | 2,6 |  |  | 284
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 351
Pipe-run (S) 13_A, Source: 1, m= 994,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 32 - 32 |  |  |  |  | 0
Pipe-run (R) 13_A, Source: 1, m= 994,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 32 - 32 |  |  |  |  | 0
Pipe-run (S) 14, Source: 1, m= 655,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 32 - 32 |  | 2,6 |  |  | 361
| PEX/AL/PE-RT System (pipes and fittings) | Coupling FT 32 - 1"FT |  | 0,4 |  |  | 24
| Brass and steel pipe couplings and fittings | Nipple, reduction, imperial 1"MT - ¾"MT |  | 0,4 |  |  | 24
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 157
Pipe-run (R) 14, Source: 1, m= 655,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 32 - 32 |  | 2,6 |  |  | 351
| PEX/AL/PE-RT System (pipes and fittings) | Coupling FT 32 - 1"FT |  | 0,4 |  |  | 23
| Brass and steel pipe couplings and fittings | Nipple, reduction, imperial 1"MT - ¾"MT |  | 0,4 |  |  | 23
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 153
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 13 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 15, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 16 - 16 |  | 3,7 |  |  | 8
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (R) 15, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 16 - 16 |  | 3,7 |  |  | 8
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (S) 15_A, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
Pipe-run (R) 15_A, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
Pipe-run (S) 16, Source: 1, m= 18,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 4,4 |  |  | 10
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 16, Source: 1, m= 18,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 4,4 |  |  | 10
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 17, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 1,0 |  |  | 2
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 16 - 16 |  | 3,7 |  |  | 1
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 14 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (R) 17, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 1,0 |  |  | 2
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 17_A, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 18, Source: 1, m= 339,0 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 32 - 32 |  | 0,7 |  |  | 97
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 25 - 25 |  | 2,6 |  |  | 120
| PEX/AL/PE-RT System (pipes and fittings) | Reduction 32 - 25 |  | 1,0 |  |  | 46
Pipe-run (R) 18, Source: 1, m= 339,0 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 32 - 32 |  | 0,7 |  |  | 95
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 25 - 25 |  | 2,6 |  |  | 117
| PEX/AL/PE-RT System (pipes and fittings) | Reduction 32 - 25 |  | 1,0 |  |  | 45
Pipe-run (S) 18_A, Source: 1, m= 339,0 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 18
|  | Pipe bend |  | 0,4 |  |  | 18
Pipe-run (R) 18_A, Source: 1, m= 339,0 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 15 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 18
|  | Pipe bend |  | 0,4 |  |  | 18
Pipe-run (S) 19, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 16 - 16 |  | 3,7 |  |  | 8
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (R) 19, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 16 - 16 |  | 3,7 |  |  | 8
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (S) 19_A, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
Pipe-run (R) 19_A, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
Pipe-run (S) 2, Source: 1, m= 1922,2 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 50 - 40 - 50 |  | 2,6 |  |  | 407
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 40 |  |  |  |  | 0
Pipe-run (R) 2, Source: 1, m= 1922,2 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 50 - 40 - 50 |  | 2,6 |  |  | 396
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 40 |  |  |  |  | 0
Pipe-run (S) 20, Source: 1, m= 18,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 4,4 |  |  | 10
|  | Pipe bend |  | 0,4 |  |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 16 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 20, Source: 1, m= 18,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 4,4 |  |  | 10
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 21, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 1,0 |  |  | 2
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 16 - 16 |  | 3,7 |  |  | 1
Pipe-run (R) 21, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 1,0 |  |  | 2
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 21_A, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 22, Source: 1, m= 850,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  | 1,4 |  |  | 157
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 264
Pipe-run (R) 22, Source: 1, m= 850,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 17 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  | 1,4 |  |  | 153
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 257
Pipe-run (S) 22_A, Source: 1, m= 850,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 264
Pipe-run (R) 22_A, Source: 1, m= 850,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 257
Pipe-run (S) 22_B, Source: 1, m= 850,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  |  |  |  | 0
Pipe-run (R) 22_B, Source: 1, m= 850,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  |  |  |  | 0
Pipe-run (S) 23, Source: 1, m= 501,8 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  | 3,1 |  |  | 315
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 40
|  | Pipe bend |  | 0,4 |  |  | 40
Pipe-run (R) 23, Source: 1, m= 501,8 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  | 3,1 |  |  | 306
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 39
|  | Pipe bend |  | 0,4 |  |  | 39
Pipe-run (S) 24, Source: 1, m= 23,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 1
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 18 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (R) 24, Source: 1, m= 23,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 1
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (S) 25, Source: 1, m= 11,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 25, Source: 1, m= 11,9 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 26, Source: 1, m= 11,9 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 26, Source: 1, m= 11,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 19 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 27, Source: 1, m= 348,5 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  | 1,4 |  |  | 142
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 25 - 25 |  | 2,6 |  |  | 127
Pipe-run (R) 27, Source: 1, m= 348,5 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  | 1,4 |  |  | 138
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 25 - 25 |  | 2,6 |  |  | 123
Pipe-run (S) 27_A, Source: 1, m= 348,5 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 19
|  | Pipe bend |  | 0,4 |  |  | 19
Pipe-run (R) 27_A, Source: 1, m= 348,5 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 19
|  | Pipe bend |  | 0,4 |  |  | 19
Pipe-run (S) 28, Source: 1, m= 23,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (R) 28, Source: 1, m= 23,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 1
|  | Pipe bend |  | 0,4 |  |  | 1
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 20 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 29, Source: 1, m= 11,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 29, Source: 1, m= 11,9 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 3, Source: 1, m= 848,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 40 |  | 2,6 |  |  | 588
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 263
Pipe-run (R) 3, Source: 1, m= 848,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 40 |  | 2,6 |  |  | 573
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 256
Pipe-run (S) 3_A, Source: 1, m= 848,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  |  |  |  | 0
Pipe-run (R) 3_A, Source: 1, m= 848,6 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  |  |  |  | 0
Pipe-run (S) 30, Source: 1, m= 11,9 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 21 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 30, Source: 1, m= 11,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 31, Source: 1, m= 1543,0 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 50 - 40 - 50 |  | 1,4 |  |  | 219
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 40 - 40 |  | 2,1 |  |  | 306
| PEX/AL/PE-RT System (pipes and fittings) | Reduction 50 - 40 |  | 0,9 |  |  | 131
Pipe-run (R) 31, Source: 1, m= 1543,0 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 50 - 40 - 50 |  | 1,4 |  |  | 213
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 40 - 40 |  | 2,1 |  |  | 298
| PEX/AL/PE-RT System (pipes and fittings) | Reduction 50 - 40 |  | 0,9 |  |  | 128
Pipe-run (S) 31_A, Source: 1, m= 1543,0 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 40 - 40 |  | 2,1 |  |  | 306
Pipe-run (R) 31_A, Source: 1, m= 1543,0 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 40 - 40 |  | 2,1 |  |  | 298
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 22 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 31_B, Source: 1, m= 1543,0 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  |  |  |  | 0
Pipe-run (R) 31_B, Source: 1, m= 1543,0 kg/h, Diameter: 40 x 4,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 42 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  |  |  |  | 0
Pipe-run (S) 32, Source: 1, m= 822,8 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  | 2,6 |  |  | 379
| PEX/AL/PE-RT System (pipes and fittings) | Coupling FT 32 - 1"FT |  | 0,4 |  |  | 38
| Brass and steel pipe couplings and fittings | Nipple, reduction, imperial 1"MT - ¾"MT |  | 0,4 |  |  | 38
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 247
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 247
Pipe-run (R) 32, Source: 1, m= 822,8 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  | 2,6 |  |  | 369
| PEX/AL/PE-RT System (pipes and fittings) | Coupling FT 32 - 1"FT |  | 0,4 |  |  | 37
| Brass and steel pipe couplings and fittings | Nipple, reduction, imperial 1"MT - ¾"MT |  | 0,4 |  |  | 37
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 241
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 241
Pipe-run (S) 33, Source: 1, m= 35,8 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 2
Pipe-run (R) 33, Source: 1, m= 35,8 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 2
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 23 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 34, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 15
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
Pipe-run (R) 34, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 15
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
Pipe-run (S) 35, Source: 1, m= 18,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 4,4 |  |  | 10
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 35, Source: 1, m= 18,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 4,4 |  |  | 10
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 36, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 1,0 |  |  | 2
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 36, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 1,0 |  |  | 2
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 24 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 37, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 15
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 37, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 15
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 38, Source: 1, m= 720,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  | 1,4 |  |  | 204
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 190
Pipe-run (R) 38, Source: 1, m= 720,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 40 - 32 - 32 |  | 1,4 |  |  | 199
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 185
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 25 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 38_A, Source: 1, m= 720,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Coupling FT 32 - 1"FT |  | 0,4 |  |  | 29
| Brass and steel pipe couplings and fittings | Nipple, reduction, imperial 1"MT - ¾"MT |  | 0,4 |  |  | 29
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 189
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 189
Pipe-run (R) 38_A, Source: 1, m= 720,3 kg/h, Diameter: 32 x 3,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 35 mm. Thickness = 40 mm
| PEX/AL/PE-RT System (pipes and fittings) | Coupling FT 32 - 1"FT |  | 0,4 |  |  | 28
| Brass and steel pipe couplings and fittings | Nipple, reduction, imperial 1"MT - ¾"MT |  | 0,4 |  |  | 28
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 185
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 32 - 32 |  | 2,6 |  |  | 185
Pipe-run (S) 39, Source: 1, m= 35,8 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 2
Pipe-run (R) 39, Source: 1, m= 35,8 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 2
Pipe-run (S) 4, Source: 1, m= 500,8 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  | 3,1 |  |  | 314
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 40
|  | Pipe bend |  | 0,4 |  |  | 40
Pipe-run (R) 4, Source: 1, m= 500,8 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  | 3,1 |  |  | 305
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 26 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 39
|  | Pipe bend |  | 0,4 |  |  | 39
Pipe-run (S) 40, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 15
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
Pipe-run (R) 40, Source: 1, m= 27,2 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 15
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
Pipe-run (S) 41, Source: 1, m= 18,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 4,4 |  |  | 10
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 41, Source: 1, m= 18,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 4,4 |  |  | 10
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 42, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 1,0 |  |  | 2
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 27 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (R) 42, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 1,0 |  |  | 2
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 43, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 15
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 43, Source: 1, m= 8,6 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 15
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 5, Source: 1, m= 23,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 1
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (R) 5, Source: 1, m= 23,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 28 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (S) 6, Source: 1, m= 11,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 6, Source: 1, m= 11,9 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (S) 7, Source: 1, m= 11,9 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
Pipe-run (R) 7, Source: 1, m= 11,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  | 3,9 |  |  | 7
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 29 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv |  | Pressure drop
[5 empty] | m³/h |  | Pa
Pipe-run (S) 8, Source: 1, m= 347,8 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  | 1,4 |  |  | 142
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 25 - 25 |  | 2,6 |  |  | 126
Pipe-run (R) 8, Source: 1, m= 347,8 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 32 - 25 - 25 |  | 1,4 |  |  | 138
| PEX/AL/PE-RT System (pipes and fittings) | Elbow 90° 25 - 25 |  | 2,6 |  |  | 123
Pipe-run (S) 8_A, Source: 1, m= 347,8 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 19
|  | Pipe bend |  | 0,4 |  |  | 19
Pipe-run (R) 8_A, Source: 1, m= 347,8 kg/h, Diameter: 25 x 2,5 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 25 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Coupling MT 25 - ¾"MT |  | 0,4 |  |  | 19
|  | Pipe bend |  | 0,4 |  |  | 19
Pipe-run (S) 9, Source: 1, m= 23,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 1
|  | Pipe bend |  | 0,4 |  |  | 1
Pipe-run (R) 9, Source: 1, m= 23,5 kg/h, Diameter: 16 x 2,0 mm, Insulation: PU foam lagging, λ(20°C)=0,036W/mK Int. diam. = 18 mm. Thickness = 25 mm
| PEX/AL/PE-RT System (pipes and fittings) | Tee 16 - 16 - 16 |  |  |  |  | 0
|  | Pipe bend |  | 0,4 |  |  | 1
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 30 -

## List of rooms - heating
Project:
List of rooms - heating
Room Symbol |  |  |  |  | Room surface area |  | Thermal resistance of covering |  |  | Design room temperature |  | Heat loss in room | Required output of heating | Required specific heating output | Required radiant heating output | Required convection heating output | Obtained radiant heating output | Obtained convection heating output | Output recovered from pipe-runs | Coverage of required heating output
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [18 empty] | - 31 -
Project:
Room |  |  |  |  | A |  | Rλ,B |  |  | θi,H |  | Φstd,H | Φreq,H | qreq,H | Φreq,rad,H | Φreq,conv,H | Φrh,H | Φconv,H | Φpipe,H | %Φreq,H
[5 empty] | m² |  | (m²·K)/W |  |  | °C |  | W | W | W/m² | W | W | W | W | W | %
| Bld. unit: |  |  | 02
| 101 Living room |  |  |  | 43,29 |  | 0,071 |  |  | 20,0 |  | 2165 | 2165 | 50,00 | 1948 | 216 | 2023 | 350 | 0 | 110
| 102 Living room |  |  |  | 20,73 |  | 0,071 |  |  | 20,0 |  | 1036 | 1036 | 50,00 | 1036 | 0 | 1036 | 0 | 0 | 100
| 103 Living room |  |  |  | 26,83 |  | 0,071 |  |  | 20,0 |  | 1342 | 1342 | 50,00 | 1207 | 134 | 1207 | 255 | 0 | 109
| 104 Living room |  |  |  | 43,29 |  | 0,071 |  |  | 20,0 |  | 2165 | 2165 | 50,00 | 1948 | 216 | 1752 | 350 | 0 | 97
| 105 Living room |  |  |  | 20,73 |  | 0,071 |  |  | 20,0 |  | 1036 | 1036 | 50,00 | 1036 | 0 | 1003 | 0 | 0 | 97
| 106 Living room |  |  |  | 26,83 |  | 0,071 |  |  | 20,0 |  | 1341 | 1341 | 50,00 | 1207 | 134 | 1207 | 256 | 0 | 109
| 107 Living room |  |  |  | 2,62 |  | 0,071 |  |  | 20,0 |  | 131 | 131 | 50,00 | 131 | 0 | 131 | 0 | 0 | 100
| 108 Bedroom |  |  |  | 5,06 |  | 0,071 |  |  | 20,0 |  | 253 | 253 | 50,00 | 253 | 0 | 253 | 0 | 0 | 100
| 109 Bathroom |  |  |  | 5,13 |  | 0,100 |  |  | 24,0 |  | 284 | 284 | 55,26 | 199 | 85 | 155 | 203 | 0 | 126
| 110 Living room |  |  |  | 2,61 |  | 0,071 |  |  | 20,0 |  | 131 | 131 | 50,00 | 131 | 0 | 131 | 0 | 0 | 100
| 111 Bathroom |  |  |  | 3,63 |  | 0,100 |  |  | 24,0 |  | 201 | 201 | 55,26 | 120 | 80 | 99 | 202 | 0 | 150
| 112 Bathroom |  |  |  | 3,62 |  | 0,100 |  |  | 24,0 |  | 200 | 200 | 55,26 | 120 | 80 | 120 | 197 | 0 | 158
| 113 Living room |  |  |  | 11,37 |  | 0,071 |  |  | 20,0 |  | 568 | 568 | 50,00 | 568 | 0 | 568 | 0 | 0 | 100
| 114 Living room |  |  |  | 11,37 |  | 0,071 |  |  | 20,0 |  | 568 | 568 | 50,00 | 568 | 0 | 568 | 0 | 0 | 100
| 115 Bathroom |  |  |  | 6,29 |  | 0,100 |  |  | 24,0 |  | 347 | 347 | 55,26 | 208 | 139 | 178 | 217 | 0 | 114
| 116 Bathroom |  |  |  | 6,29 |  | 0,100 |  |  | 24,0 |  | 347 | 347 | 55,26 | 208 | 139 | 166 | 219 | 0 | 111
| 117 Living room |  |  |  | 11,68 |  | 0,071 |  |  | 20,0 |  | 584 | 584 | 50,00 | 584 | 0 | 584 | 0 | 0 | 100
| 118 Living room |  |  |  | 11,68 |  | 0,071 |  |  | 20,0 |  | 584 | 584 | 50,00 | 584 | 0 | 584 | 0 | 0 | 100
Storey: |  | 2 | Second floor, |  |  |  |  | Elevation |  |  | 3,3 m
| Bld. unit: |  |  | 08
| 201 Living room |  |  |  | 43,29 |  | 0,071 |  |  | 20,0 |  | 2165 | 2165 | 50,00 | 1948 | 216 | 2028 | 349 | 0 | 110
| 202 Living room |  |  |  | 20,73 |  | 0,071 |  |  | 20,0 |  | 1036 | 1036 | 50,00 | 1036 | 0 | 1036 | 0 | 0 | 100
| 203 Living room |  |  |  | 26,83 |  | 0,071 |  |  | 20,0 |  | 1342 | 1342 | 50,00 | 1207 | 134 | 1207 | 254 | 0 | 109
| 204 Living room |  |  |  | 43,29 |  | 0,071 |  |  | 20,0 |  | 2165 | 2165 | 50,00 | 1948 | 216 | 1805 | 350 | 0 | 100
| 205 Living room |  |  |  | 20,73 |  | 0,071 |  |  | 20,0 |  | 1036 | 1036 | 50,00 | 1036 | 0 | 1003 | 0 | 0 | 97
| 206 Living room |  |  |  | 26,83 |  | 0,071 |  |  | 20,0 |  | 1341 | 1341 | 50,00 | 1207 | 134 | 1207 | 255 | 0 | 109
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [18 empty] | - 32 -
Project:
Room |  |  |  |  | A |  | Rλ,B |  |  | θi,H |  | Φstd,H | Φreq,H | qreq,H | Φreq,rad,H | Φreq,conv,H | Φrh,H | Φconv,H | Φpipe,H | %Φreq,H
[5 empty] | m² |  | (m²·K)/W |  |  | °C |  | W | W | W/m² | W | W | W | W | W | %
| 207 Living room |  |  |  | 2,62 |  | 0,071 |  |  | 20,0 |  | 131 | 131 | 50,00 | 131 | 0 | 131 | 0 | 0 | 100
| 208 Bedroom |  |  |  | 5,06 |  | 0,071 |  |  | 20,0 |  | 253 | 253 | 50,00 | 253 | 0 | 253 | 0 | 0 | 100
| 209 Bathroom |  |  |  | 5,13 |  | 0,100 |  |  | 24,0 |  | 284 | 284 | 55,26 | 199 | 85 | 155 | 202 | 0 | 126
| 210 Living room |  |  |  | 2,61 |  | 0,071 |  |  | 20,0 |  | 131 | 131 | 50,00 | 131 | 0 | 131 | 0 | 0 | 100
| 211 Bathroom |  |  |  | 3,63 |  | 0,100 |  |  | 24,0 |  | 201 | 201 | 55,26 | 120 | 80 | 99 | 202 | 0 | 150
| 212 Bathroom |  |  |  | 3,62 |  | 0,100 |  |  | 24,0 |  | 200 | 200 | 55,26 | 120 | 80 | 120 | 196 | 0 | 158
| 213 Living room |  |  |  | 11,37 |  | 0,071 |  |  | 20,0 |  | 568 | 568 | 50,00 | 568 | 0 | 568 | 0 | 0 | 100
| 214 Living room |  |  |  | 11,37 |  | 0,071 |  |  | 20,0 |  | 568 | 568 | 50,00 | 568 | 0 | 568 | 0 | 0 | 100
| 215 Bathroom |  |  |  | 6,29 |  | 0,100 |  |  | 24,0 |  | 347 | 347 | 55,26 | 208 | 139 | 178 | 217 | 0 | 113
| 216 Bathroom |  |  |  | 6,29 |  | 0,100 |  |  | 24,0 |  | 347 | 347 | 55,26 | 208 | 139 | 166 | 219 | 0 | 111
| 217 Living room |  |  |  | 11,68 |  | 0,071 |  |  | 20,0 |  | 584 | 584 | 50,00 | 584 | 0 | 584 | 0 | 0 | 100
| 218 Living room |  |  |  | 11,68 |  | 0,071 |  |  | 20,0 |  | 584 | 584 | 50,00 | 584 | 0 | 584 | 0 | 0 | 100
Storey: |  | 3 | Attic, |  |  | Elevation |  |  | 6,6 m
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [18 empty] | - 33 -

## Heating_cooling circuits
Project:
Heating/cooling circuits
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: 103-1-1
Storey: 1 First floor, Building unit: 02 , Room: 103 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 23 | 33353 | 501,8 | 25 x 2,5 | 0,96 | 0,46 | 125 | 3,9 | 396 | 515 | 0 |  | 515 | 25
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | -25022
| Heating/cooling floor | 103-1-1 | 752 | 142,1 | 16x2.0 | 125,0 | 0,35 |  |  |  |  | 0 |  | 22204
| Heating/cooling floor (Thermosiphon) | [12 empty] | 13
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | 38314
|  | 23 | 33343 | 501,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 385 | 535 | 0 |  | 535 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 457
Circuit through Heating/cooling floor: 114-1-1
Storey: 1 First floor, Building unit: 02 , Room: 114 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 23 | 33353 | 501,8 | 25 x 2,5 | 0,96 | 0,46 | 125 | 3,9 | 396 | 515 | 0 |  | 515 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 34 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | -25022
| Heating/cooling floor | 114-1-1 | 568 | 78,3 | 16x2.0 | 84,2 | 0,19 |  |  |  |  | 0 |  | 5285
| Heating/cooling floor (Thermosiphon) | [12 empty] | 13
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | 38314
|  | 23 | 33343 | 501,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 385 | 535 | 0 |  | 535 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 457
Circuit through Heating/cooling floor: 103-5-1
Storey: 1 First floor, Building unit: 02 , Room: 103 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 23 | 33353 | 501,8 | 25 x 2,5 | 0,96 | 0,46 | 125 | 3,9 | 396 | 515 | 0 |  | 515 | 25
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | -25022
| Heating/cooling floor | 103-5-1 | 308 | 69,8 | 16x2.0 | 60,0 | 0,17 |  |  |  |  | 0 |  | 3082
| Heating/cooling floor (Thermosiphon) | [12 empty] | 13
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | 38314
|  | 23 | 33343 | 501,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 385 | 535 | 0 |  | 535 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 457
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 35 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: 115-2-1
Storey: 1 First floor, Building unit: 02 , Room: 115 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 23 | 33353 | 501,8 | 25 x 2,5 | 0,96 | 0,46 | 125 | 3,9 | 396 | 515 | 0 |  | 515 | 25
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | -25022
| Heating/cooling floor | 115-2-1 | 178 | 47,7 | 16x2.0 | 46,5 | 0,12 |  |  |  |  | 0 |  | 872
| Heating/cooling floor (Thermosiphon) | [12 empty] | 11
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | 38314
|  | 23 | 33343 | 501,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 385 | 535 | 0 |  | 535 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 457
Circuit through Heating/cooling floor: 106-2-1
Storey: 1 First floor, Building unit: 02 , Room: 106 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 4 | 33332 | 500,8 | 25 x 2,5 | 0,96 | 0,45 | 125 | 3,9 | 394 | 514 | 0 |  | 514 | 25
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | -21156
| Heating/cooling floor | 106-2-1 | 727 | 132,4 | 16x2.0 | 119,3 | 0,33 |  |  |  |  | 0 |  | 18743
| Heating/cooling floor (Thermosiphon) | [12 empty] | 11
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | 39858
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 36 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 4 | 33322 | 500,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 384 | 533 | 0 |  | 533 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 457
Circuit through Heating/cooling floor: 113-1-1
Storey: 1 First floor, Building unit: 02 , Room: 113 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 4 | 33332 | 500,8 | 25 x 2,5 | 0,96 | 0,45 | 125 | 3,9 | 394 | 514 | 0 |  | 514 | 25
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | -21156
| Heating/cooling floor | 113-1-1 | 568 | 75,0 | 16x2.0 | 84,7 | 0,18 |  |  |  |  | 0 |  | 4937
| Heating/cooling floor (Thermosiphon) | [12 empty] | 11
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | 39858
|  | 4 | 33322 | 500,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 384 | 533 | 0 |  | 533 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 457
Circuit through Heating/cooling floor: 116-2-1
Storey: 1 First floor, Building unit: 02 , Room: 116 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 4 | 33332 | 500,8 | 25 x 2,5 | 0,96 | 0,45 | 125 | 3,9 | 394 | 514 | 0 |  | 514 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 37 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | -21156
| Heating/cooling floor | 116-2-1 | 166 | 60,9 | 16x2.0 | 60,8 | 0,15 |  |  |  |  | 0 |  | 2445
| Heating/cooling floor (Thermosiphon) | [12 empty] | 8
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | 39858
|  | 4 | 33322 | 500,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 384 | 533 | 0 |  | 533 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 457
Circuit through Heating/cooling floor: 106-1-1
Storey: 1 First floor, Building unit: 02 , Room: 106 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 4 | 33332 | 500,8 | 25 x 2,5 | 0,96 | 0,45 | 125 | 3,9 | 394 | 514 | 0 |  | 514 | 25
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | -21156
| Heating/cooling floor | 106-1-1 | 300 | 59,1 | 16x2.0 | 58,0 | 0,15 |  |  |  |  | 0 |  | 1404
| Heating/cooling floor (Thermosiphon) | [12 empty] | 11
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | 39858
|  | 4 | 33322 | 500,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 384 | 533 | 0 |  | 533 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 457
Circuit through Heating/cooling floor: 101-5-1
Storey: 1 First floor, Building unit: 02 , Room: 101 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 38 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -17104
| Heating/cooling floor | 101-5-1 | 882 | 150,2 | 16x2.0 | 83,4 | 0,37 |  |  |  |  | 0 |  | 15969
| Heating/cooling floor (Thermosiphon) | [12 empty] | 16
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | 37967
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 461
Circuit through Heating/cooling floor: 102-2-1
Storey: 1 First floor, Building unit: 02 , Room: 102 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -17104
| Heating/cooling floor | 102-2-1 | 885 | 118,5 | 16x2.0 | 70,6 | 0,29 |  |  |  |  | 0 |  | 8878
| Heating/cooling floor (Thermosiphon) | [12 empty] | 14
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | 37967
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 39 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 461
Circuit through Heating/cooling floor: 101-5-2
Storey: 1 First floor, Building unit: 02 , Room: 101 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -17104
| Heating/cooling floor | 101-5-2 | 591 | 101,4 | 16x2.0 | 80,2 | 0,25 |  |  |  |  | 0 |  | 7796
| Heating/cooling floor (Thermosiphon) | [12 empty] | 18
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | 37967
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 461
Circuit through Heating/cooling floor: 117-1-1
Storey: 1 First floor, Building unit: 02 , Room: 117 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -17104
| Heating/cooling floor | 117-1-1 | 584 | 62,6 | 16x2.0 | 57,2 | 0,15 |  |  |  |  | 0 |  | 2387
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 40 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Heating/cooling floor (Thermosiphon) | [12 empty] | 16
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | 37967
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 461
Circuit through Heating/cooling floor: 112-2-1
Storey: 1 First floor, Building unit: 02 , Room: 112 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -17104
| Heating/cooling floor | 112-2-1 | 120 | 32,6 | 16x2.0 | 29,0 | 0,08 |  |  |  |  | 0 |  | 341
| Heating/cooling floor (Thermosiphon) | [12 empty] | 13
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | 37967
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 461
Circuit through Heating/cooling floor: 108-1-1
Storey: 1 First floor, Building unit: 02 , Room: 108 Bedroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 41 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -17104
| Heating/cooling floor | 108-1-1 | 253 | 32,7 | 16x2.0 | 24,4 | 0,08 |  |  |  |  | 0 |  | 294
| Heating/cooling floor (Thermosiphon) | [12 empty] | 14
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | 37967
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 461
Circuit through Heating/cooling floor: 102-1-1
Storey: 1 First floor, Building unit: 02 , Room: 102 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -17104
| Heating/cooling floor | 102-1-1 | 151 | 23,9 | 16x2.0 | 26,4 | 0,06 |  |  |  |  | 0 |  | 232
| Heating/cooling floor (Thermosiphon) | [12 empty] | 14
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | 37967
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 42 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 461
Circuit through Heating/cooling floor: 107-1-1
Storey: 1 First floor, Building unit: 02 , Room: 107 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -17104
| Heating/cooling floor | 107-1-1 | 131 | 16,0 | 16x2.0 | 25,2 | 0,04 |  |  |  |  | 0 |  | 155
| Heating/cooling floor (Thermosiphon) | [12 empty] | 17
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | 37967
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 461
Circuit through Heating/cooling floor: 203-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 203 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 27 | 23834 | 348,5 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 269 | 486 | 0 |  | 486 | 25
|  | 27_A | 23796 | 348,5 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | -13577
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 43 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Heating/cooling floor | 203-1-1 | 752 | 94,3 | 16x2.0 | 125,0 | 0,23 |  |  |  |  | 0 |  | 10856
| Heating/cooling floor (Thermosiphon) | [12 empty] | 77
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | 39879
|  | 27_A | 23785 | 348,5 | 25 x 2,5 | 0,96 | 0,31 | 84 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 27 | 23782 | 348,5 | 25 x 2,5 | 3,30 | 0,31 | 84 | 4,0 | 262 | 537 | 0 |  | 537 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1100
Circuit through Heating/cooling floor: 214-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 214 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 27 | 23834 | 348,5 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 269 | 486 | 0 |  | 486 | 25
|  | 27_A | 23796 | 348,5 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | -13577
| Heating/cooling floor | 214-1-1 | 568 | 78,3 | 16x2.0 | 84,2 | 0,19 |  |  |  |  | 0 |  | 5283
| Heating/cooling floor (Thermosiphon) | [12 empty] | 75
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | 39879
|  | 27_A | 23785 | 348,5 | 25 x 2,5 | 0,96 | 0,31 | 84 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 27 | 23782 | 348,5 | 25 x 2,5 | 3,30 | 0,31 | 84 | 4,0 | 262 | 537 | 0 |  | 537 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1100
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 44 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: 203-5-1
Storey: 2 Second floor, Building unit: 08 , Room: 203 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 27 | 23834 | 348,5 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 269 | 486 | 0 |  | 486 | 25
|  | 27_A | 23796 | 348,5 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | -13577
| Heating/cooling floor | 203-5-1 | 308 | 55,3 | 16x2.0 | 60,0 | 0,14 |  |  |  |  | 0 |  | 1329
| Heating/cooling floor (Thermosiphon) | [12 empty] | 68
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | 39879
|  | 27_A | 23785 | 348,5 | 25 x 2,5 | 0,96 | 0,31 | 84 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 27 | 23782 | 348,5 | 25 x 2,5 | 3,30 | 0,31 | 84 | 4,0 | 262 | 537 | 0 |  | 537 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1100
Circuit through Heating/cooling floor: 215-2-1
Storey: 2 Second floor, Building unit: 08 , Room: 215 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 27 | 23834 | 348,5 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 269 | 486 | 0 |  | 486 | 25
|  | 27_A | 23796 | 348,5 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | -13577
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 45 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Heating/cooling floor | 215-2-1 | 178 | 44,2 | 16x2.0 | 46,5 | 0,11 |  |  |  |  | 0 |  | 810
| Heating/cooling floor (Thermosiphon) | [12 empty] | 59
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | 39879
|  | 27_A | 23785 | 348,5 | 25 x 2,5 | 0,96 | 0,31 | 84 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 27 | 23782 | 348,5 | 25 x 2,5 | 3,30 | 0,31 | 84 | 4,0 | 262 | 537 | 0 |  | 537 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1100
Circuit through Heating/cooling floor: 206-2-1
Storey: 2 Second floor, Building unit: 08 , Room: 206 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 8 | 23818 | 347,8 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 268 | 484 | 0 |  | 484 | 25
|  | 8_A | 23780 | 347,8 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | -11597
| Heating/cooling floor | 206-2-1 | 727 | 87,0 | 16x2.0 | 119,3 | 0,21 |  |  |  |  | 0 |  | 9013
| Heating/cooling floor (Thermosiphon) | [12 empty] | 79
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | 41632
|  | 8_A | 23769 | 347,8 | 25 x 2,5 | 0,96 | 0,31 | 83 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 8 | 23766 | 347,8 | 25 x 2,5 | 3,30 | 0,31 | 83 | 4,0 | 261 | 535 | 0 |  | 535 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1100
Circuit through Heating/cooling floor: 213-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 213 Living room
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 46 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 8 | 23818 | 347,8 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 268 | 484 | 0 |  | 484 | 25
|  | 8_A | 23780 | 347,8 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | -11597
| Heating/cooling floor | 213-1-1 | 568 | 75,0 | 16x2.0 | 84,7 | 0,18 |  |  |  |  | 0 |  | 4937
| Heating/cooling floor (Thermosiphon) | [12 empty] | 76
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | 41632
|  | 8_A | 23769 | 347,8 | 25 x 2,5 | 0,96 | 0,31 | 83 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 8 | 23766 | 347,8 | 25 x 2,5 | 3,30 | 0,31 | 83 | 4,0 | 261 | 535 | 0 |  | 535 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1100
Circuit through Heating/cooling floor: 216-2-1
Storey: 2 Second floor, Building unit: 08 , Room: 216 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 8 | 23818 | 347,8 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 268 | 484 | 0 |  | 484 | 25
|  | 8_A | 23780 | 347,8 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | -11597
| Heating/cooling floor | 216-2-1 | 166 | 56,6 | 16x2.0 | 60,8 | 0,14 |  |  |  |  | 0 |  | 1353
| Heating/cooling floor (Thermosiphon) | [12 empty] | 59
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | 41632
|  | 8_A | 23769 | 347,8 | 25 x 2,5 | 0,96 | 0,31 | 83 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 8 | 23766 | 347,8 | 25 x 2,5 | 3,30 | 0,31 | 83 | 4,0 | 261 | 535 | 0 |  | 535 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 47 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1100
Circuit through Heating/cooling floor: 206-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 206 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 8 | 23818 | 347,8 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 268 | 484 | 0 |  | 484 | 25
|  | 8_A | 23780 | 347,8 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | -11597
| Heating/cooling floor | 206-1-1 | 300 | 46,0 | 16x2.0 | 58,0 | 0,11 |  |  |  |  | 0 |  | 1076
| Heating/cooling floor (Thermosiphon) | [12 empty] | 72
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | 41632
|  | 8_A | 23769 | 347,8 | 25 x 2,5 | 0,96 | 0,31 | 83 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 8 | 23766 | 347,8 | 25 x 2,5 | 3,30 | 0,31 | 83 | 4,0 | 261 | 535 | 0 |  | 535 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1100
Circuit through Heating/cooling floor: 202-2-1
Storey: 2 Second floor, Building unit: 08 , Room: 202 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 48 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -10783
| Heating/cooling floor | 202-2-1 | 885 | 118,5 | 16x2.0 | 70,6 | 0,29 |  |  |  |  | 0 |  | 8873
| Heating/cooling floor (Thermosiphon) | [12 empty] | 99
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | 40446
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1116
Circuit through Heating/cooling floor: 201-5-1
Storey: 2 Second floor, Building unit: 08 , Room: 201 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -10783
| Heating/cooling floor | 201-5-1 | 806 | 64,6 | 16x2.0 | 98,6 | 0,16 |  |  |  |  | 0 |  | 4401
| Heating/cooling floor (Thermosiphon) | [12 empty] | 136
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | 40446
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1116
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 49 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: 201-5-2
Storey: 2 Second floor, Building unit: 08 , Room: 201 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -10783
| Heating/cooling floor | 201-5-2 | 667 | 60,1 | 16x2.0 | 97,6 | 0,15 |  |  |  |  | 0 |  | 3845
| Heating/cooling floor (Thermosiphon) | [12 empty] | 138
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | 40446
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1116
Circuit through Heating/cooling floor: 217-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 217 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -10783
| Heating/cooling floor | 217-1-1 | 584 | 62,6 | 16x2.0 | 57,2 | 0,15 |  |  |  |  | 0 |  | 2384
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 50 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Heating/cooling floor (Thermosiphon) | [12 empty] | 113
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | 40446
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1116
Circuit through Heating/cooling floor: 212-2-1
Storey: 2 Second floor, Building unit: 08 , Room: 212 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -10783
| Heating/cooling floor | 212-2-1 | 120 | 30,6 | 16x2.0 | 29,0 | 0,08 |  |  |  |  | 0 |  | 320
| Heating/cooling floor (Thermosiphon) | [12 empty] | 90
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | 40446
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1116
Circuit through Heating/cooling floor: 208-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 208 Bedroom
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 51 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -10783
| Heating/cooling floor | 208-1-1 | 253 | 32,7 | 16x2.0 | 24,4 | 0,08 |  |  |  |  | 0 |  | 294
| Heating/cooling floor (Thermosiphon) | [12 empty] | 101
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | 40446
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1116
Circuit through Heating/cooling floor: 202-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 202 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -10783
| Heating/cooling floor | 202-1-1 | 151 | 23,8 | 16x2.0 | 26,4 | 0,06 |  |  |  |  | 0 |  | 232
| Heating/cooling floor (Thermosiphon) | [12 empty] | 101
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | 40446
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 52 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1116
Circuit through Heating/cooling floor: 207-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 207 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -10783
| Heating/cooling floor | 207-1-1 | 131 | 16,0 | 16x2.0 | 25,2 | 0,04 |  |  |  |  | 0 |  | 154
| Heating/cooling floor (Thermosiphon) | [12 empty] | 121
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | 40446
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1116
Circuit through Heating/cooling floor: 205-2-1
Storey: 2 Second floor, Building unit: 08 , Room: 205 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 53 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -5063
| Heating/cooling floor | 205-2-1 | 875 | 73,3 | 16x2.0 | 77,5 | 0,18 |  |  |  |  | 0 |  | 4264
| Heating/cooling floor (Thermosiphon) | [12 empty] | 153
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | 41838
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1068
Circuit through Heating/cooling floor: 218-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 218 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -5063
| Heating/cooling floor | 218-1-1 | 584 | 55,9 | 16x2.0 | 84,5 | 0,14 |  |  |  |  | 0 |  | 2893
| Heating/cooling floor (Thermosiphon) | [12 empty] | 146
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | 41838
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1068
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 54 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: 204-4-2
Storey: 2 Second floor, Building unit: 08 , Room: 204 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -5063
| Heating/cooling floor | 204-4-2 | 748 | 52,2 | 16x2.0 | 87,8 | 0,13 |  |  |  |  | 0 |  | 1830
| Heating/cooling floor (Thermosiphon) | [12 empty] | 173
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | 41838
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1068
Circuit through Heating/cooling floor: 204-4-1
Storey: 2 Second floor, Building unit: 08 , Room: 204 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -5063
| Heating/cooling floor | 204-4-1 | 494 | 41,4 | 16x2.0 | 79,6 | 0,10 |  |  |  |  | 0 |  | 1317
| Heating/cooling floor (Thermosiphon) | [12 empty] | 173
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | 41838
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 55 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1068
Circuit through Heating/cooling floor: 211-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 211 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -5063
| Heating/cooling floor | 211-1-1 | 99 | 38,3 | 16x2.0 | 24,7 | 0,09 |  |  |  |  | 0 |  | 334
| Heating/cooling floor (Thermosiphon) | [12 empty] | 110
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | 41838
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1068
Circuit through Heating/cooling floor: 209-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 209 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 56 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -5063
| Heating/cooling floor | 209-1-1 | 155 | 36,2 | 16x2.0 | 20,0 | 0,09 |  |  |  |  | 0 |  | 255
| Heating/cooling floor (Thermosiphon) | [12 empty] | 110
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | 41838
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1068
Circuit through Heating/cooling floor: 205-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 205 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -5063
| Heating/cooling floor | 205-1-1 | 128 | 16,3 | 16x2.0 | 29,2 | 0,04 |  |  |  |  | 0 |  | 184
| Heating/cooling floor (Thermosiphon) | [12 empty] | 159
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | 41838
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1068
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 57 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: 210-1-1
Storey: 2 Second floor, Building unit: 08 , Room: 210 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -5063
| Heating/cooling floor | 210-1-1 | 131 | 16,5 | 16x2.0 | 24,7 | 0,04 |  |  |  |  | 0 |  | 156
| Heating/cooling floor (Thermosiphon) | [12 empty] | 153
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | 41838
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1068
Circuit through Heating/cooling floor: 104-4-2
Storey: 1 First floor, Building unit: 02 , Room: 104 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -4583
| Heating/cooling floor | 104-4-2 | 685 | 81,2 | 16x2.0 | 80,2 | 0,20 |  |  |  |  | 0 |  | 5341
| Heating/cooling floor (Thermosiphon) | [12 empty] | 24
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | 39635
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 58 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 441
Circuit through Heating/cooling floor: 105-2-1
Storey: 1 First floor, Building unit: 02 , Room: 105 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -4583
| Heating/cooling floor | 105-2-1 | 875 | 73,3 | 16x2.0 | 77,5 | 0,18 |  |  |  |  | 0 |  | 4264
| Heating/cooling floor (Thermosiphon) | [12 empty] | 22
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | 39635
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 441
Circuit through Heating/cooling floor: 104-4-1
Storey: 1 First floor, Building unit: 02 , Room: 104 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -4583
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 59 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Heating/cooling floor | 104-4-1 | 504 | 70,7 | 16x2.0 | 75,7 | 0,17 |  |  |  |  | 0 |  | 3956
| Heating/cooling floor (Thermosiphon) | [12 empty] | 24
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | 39635
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 441
Circuit through Heating/cooling floor: 118-1-1
Storey: 1 First floor, Building unit: 02 , Room: 118 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -4583
| Heating/cooling floor | 118-1-1 | 584 | 55,9 | 16x2.0 | 84,5 | 0,14 |  |  |  |  | 0 |  | 2893
| Heating/cooling floor (Thermosiphon) | [12 empty] | 21
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | 39635
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 441
Circuit through Heating/cooling floor: 111-1-1
Storey: 1 First floor, Building unit: 02 , Room: 111 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 60 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -4583
| Heating/cooling floor | 111-1-1 | 99 | 40,6 | 16x2.0 | 24,7 | 0,10 |  |  |  |  | 0 |  | 354
| Heating/cooling floor (Thermosiphon) | [12 empty] | 16
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | 39635
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 441
Circuit through Heating/cooling floor: 109-1-1
Storey: 1 First floor, Building unit: 02 , Room: 109 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -4583
| Heating/cooling floor | 109-1-1 | 155 | 38,6 | 16x2.0 | 20,0 | 0,09 |  |  |  |  | 0 |  | 272
| Heating/cooling floor (Thermosiphon) | [12 empty] | 16
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | 39635
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 441
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 61 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Heating/cooling floor: 105-1-1
Storey: 1 First floor, Building unit: 02 , Room: 105 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -4583
| Heating/cooling floor | 105-1-1 | 128 | 16,3 | 16x2.0 | 29,3 | 0,04 |  |  |  |  | 0 |  | 184
| Heating/cooling floor (Thermosiphon) | [12 empty] | 22
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | 39635
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 441
Circuit through Heating/cooling floor: 110-1-1
Storey: 1 First floor, Building unit: 02 , Room: 110 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -4583
| Heating/cooling floor | 110-1-1 | 131 | 16,5 | 16x2.0 | 24,7 | 0,04 |  |  |  |  | 0 |  | 156
| Heating/cooling floor (Thermosiphon) | [12 empty] | 22
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | 39635
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 62 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 441
Circuit through Radiator: 212-1
Storey: 2 Second floor, Building unit: 08 , Room: 212 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -748
|  | 19 | 648 | 27,2 | 16 x 2,0 | 0,78 | 0,07 | 6 | 4,1 | 9 | 14 | 0 |  | 14 | 25
| (Thermosiphon) | [12 empty] | 93
|  | 19_A | 641 | 27,2 | 16 x 2,0 | 1,48 | 0,07 | 6 | 0,0 | 0 | 9 | 0 |  | 9 | 25
|  | 21 | 251 | 8,6 | 16 x 2,0 | 1,27 | 0,02 | 2 | 4,7 | 3 | 5 | 0 |  | 5 | 25
|  | 21_A | 241 | 8,6 | 16 x 2,0 | 3,14 | 0,02 | 2 | 1,2 | 0 | 6 | 0 |  | 6 | 25
| Radiator | 212-1 | 196 | 8,6 | [7 empty] | 3334 |  | 3334
| Radiator (Thermosiphon) | [12 empty] | -125
|  | 21 | 241 | 8,6 | 16 x 2,0 | 4,45 | 0,02 | 3 | 2,6 | 3 | 14 | 0 |  | 14 | 25
|  | 19_A | 641 | 27,2 | 16 x 2,0 | 1,49 | 0,07 | 8 | 0,0 | 0 | 11 | 0 |  | 11 | 25
|  | 19 | 646 | 27,2 | 16 x 2,0 | 0,82 | 0,07 | 8 | 4,1 | 9 | 16 | 0 |  | 16 | 25
| Flat station | (no name) | 4926 | 127,9 | [7 empty] | 37641 |  | 37641
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1131
Circuit through Radiator: 216-1
Storey: 2 Second floor, Building unit: 08 , Room: 216 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 63 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 8 | 23818 | 347,8 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 268 | 484 | 0 |  | 484 | 25
|  | 8_A | 23780 | 347,8 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | -744
| (Thermosiphon) | [12 empty] | 96
|  | 9 | 580 | 23,5 | 16 x 2,0 | 0,80 | 0,06 | 5 | 0,8 | 1 | 5 | 0 |  | 5 | 25
|  | 11 | 286 | 11,9 | 16 x 2,0 | 5,11 | 0,03 | 3 | 5,1 | 7 | 20 | 0 |  | 20 | 25
| Radiator | 216-1 | 219 | 11,9 | [7 empty] | 6569 |  | 6570
| Radiator (Thermosiphon) | [12 empty] | -120
|  | 10 | 286 | 11,9 | 16 x 2,0 | 5,05 | 0,03 | 3 | 5,1 | 7 | 24 | 0 |  | 24 | 25
|  | 9 | 580 | 23,5 | 16 x 2,0 | 0,84 | 0,06 | 7 | 0,4 | 1 | 6 | 0 |  | 6 | 25
| Flat station | (no name) | 2654 | 67,8 | [7 empty] | 35583 |  | 35583
|  | 8_A | 23769 | 347,8 | 25 x 2,5 | 0,96 | 0,31 | 83 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 8 | 23766 | 347,8 | 25 x 2,5 | 3,30 | 0,31 | 83 | 4,0 | 261 | 535 | 0 |  | 535 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1110
Circuit through Radiator: 215-1
Storey: 2 Second floor, Building unit: 08 , Room: 215 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 27 | 23834 | 348,5 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 269 | 486 | 0 |  | 486 | 25
|  | 27_A | 23796 | 348,5 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | -743
| (Thermosiphon) | [12 empty] | 96
|  | 28 | 584 | 23,5 | 16 x 2,0 | 0,84 | 0,06 | 5 | 0,4 | 1 | 5 | 0 |  | 5 | 25
|  | 30 | 291 | 11,9 | 16 x 2,0 | 5,58 | 0,03 | 3 | 5,1 | 7 | 21 | 0 |  | 21 | 25
| Radiator | 215-1 | 217 | 11,9 | [7 empty] | 6592 |  | 6592
| Radiator (Thermosiphon) | [12 empty] | -121
|  | 29 | 291 | 11,9 | 16 x 2,0 | 5,69 | 0,03 | 3 | 5,1 | 7 | 26 | 0 |  | 26 | 25
|  | 28 | 584 | 23,5 | 16 x 2,0 | 0,80 | 0,06 | 7 | 0,8 | 1 | 7 | 0 |  | 7 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 64 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Flat station | (no name) | 2632 | 68,2 | [7 empty] | 33628 |  | 33628
|  | 27_A | 23785 | 348,5 | 25 x 2,5 | 0,96 | 0,31 | 84 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 27 | 23782 | 348,5 | 25 x 2,5 | 3,30 | 0,31 | 84 | 4,0 | 262 | 537 | 0 |  | 537 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1110
Circuit through Radiator: 209-1
Storey: 2 Second floor, Building unit: 08 , Room: 209 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -670
| (Thermosiphon) | [12 empty] | 95
|  | 39 | 892 | 35,8 | 16 x 2,0 | 0,82 | 0,09 | 14 | 0,4 | 2 | 13 | 0 |  | 13 | 25
|  | 43 | 246 | 8,6 | 16 x 2,0 | 3,52 | 0,02 | 2 | 5,5 | 16 | 22 | 0 |  | 22 | 25
| Radiator | 209-1 | 202 | 8,6 | [7 empty] | 17895 |  | 17895
| Radiator (Thermosiphon) | [12 empty] | -133
|  | 43 | 246 | 8,6 | 16 x 2,0 | 3,52 | 0,02 | 3 | 5,5 | 16 | 25 | 0 |  | 25 | 25
|  | 39 | 892 | 35,8 | 16 x 2,0 | 0,79 | 0,09 | 10 | 0,4 | 2 | 10 | 0 |  | 10 | 25
| Flat station | (no name) | 4758 | 123,7 | [7 empty] | 24667 |  | 24667
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1084
Circuit through Radiator: 211-1
Storey: 2 Second floor, Building unit: 08 , Room: 211 Bathroom
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 65 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -670
| (Thermosiphon) | [12 empty] | 95
|  | 39 | 892 | 35,8 | 16 x 2,0 | 0,82 | 0,09 | 14 | 0,4 | 2 | 13 | 0 |  | 13 | 25
|  | 40 | 635 | 27,2 | 16 x 2,0 | 1,64 | 0,07 | 6 | 3,9 | 15 | 25 | 0 |  | 25 | 25
|  | 42 | 240 | 8,6 | 16 x 2,0 | 3,10 | 0,02 | 2 | 2,6 | 3 | 8 | 0 |  | 8 | 25
| Radiator | 211-1 | 202 | 8,6 | [7 empty] | 17863 |  | 17863
| Radiator (Thermosiphon) | [12 empty] | -126
|  | 42 | 240 | 8,6 | 16 x 2,0 | 2,97 | 0,02 | 3 | 2,6 | 3 | 10 | 0 |  | 10 | 25
|  | 40 | 635 | 27,2 | 16 x 2,0 | 1,75 | 0,07 | 8 | 3,9 | 15 | 29 | 0 |  | 29 | 25
|  | 39 | 892 | 35,8 | 16 x 2,0 | 0,79 | 0,09 | 10 | 0,4 | 2 | 10 | 0 |  | 10 | 25
| Flat station | (no name) | 4758 | 123,7 | [7 empty] | 24667 |  | 24667
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1084
Circuit through Radiator: 201-1
Storey: 2 Second floor, Building unit: 08 , Room: 201 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 4926 | 127,9 | [9 empty] | -748
|  | 19 | 648 | 27,2 | 16 x 2,0 | 0,78 | 0,07 | 6 | 4,1 | 9 | 14 | 0 |  | 14 | 25
| (Thermosiphon) | [12 empty] | 93
|  | 19_A | 641 | 27,2 | 16 x 2,0 | 1,48 | 0,07 | 6 | 0,0 | 0 | 9 | 0 |  | 9 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 66 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 20 | 370 | 18,6 | 16 x 2,0 | 1,55 | 0,05 | 4 | 5,2 | 11 | 17 | 0 |  | 17 | 25
| Radiator | 201-1 | 349 | 18,6 | [7 empty] | 3209 |  | 3216
| Radiator (Thermosiphon) | [12 empty] | -18
|  | 20 | 370 | 18,6 | 16 x 2,0 | 1,70 | 0,05 | 5 | 5,2 | 11 | 19 | 0 |  | 19 | 25
|  | 19_A | 641 | 27,2 | 16 x 2,0 | 1,49 | 0,07 | 8 | 0,0 | 0 | 11 | 0 |  | 11 | 25
|  | 19 | 646 | 27,2 | 16 x 2,0 | 0,82 | 0,07 | 8 | 4,1 | 9 | 16 | 0 |  | 16 | 25
| Flat station | (no name) | 4926 | 127,9 | [7 empty] | 37641 |  | 37641
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1131
Circuit through Radiator: 206-1
Storey: 2 Second floor, Building unit: 08 , Room: 206 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 8 | 23818 | 347,8 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 268 | 484 | 0 |  | 484 | 25
|  | 8_A | 23780 | 347,8 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2654 | 67,8 | [9 empty] | -744
| (Thermosiphon) | [12 empty] | 96
|  | 9 | 580 | 23,5 | 16 x 2,0 | 0,80 | 0,06 | 5 | 0,8 | 1 | 5 | 0 |  | 5 | 25
|  | 10 | 283 | 11,5 | 16 x 2,0 | 2,13 | 0,03 | 2 | 5,5 | 7 | 13 | 0 |  | 13 | 25
| Radiator | 206-1 | 255 | 11,5 | [7 empty] | 6485 |  | 6488
| Radiator (Thermosiphon) | [12 empty] | -21
|  | 11 | 283 | 11,5 | 16 x 2,0 | 2,23 | 0,03 | 3 | 5,1 | 7 | 14 | 0 |  | 14 | 25
|  | 9 | 580 | 23,5 | 16 x 2,0 | 0,84 | 0,06 | 7 | 0,4 | 1 | 6 | 0 |  | 6 | 25
| Flat station | (no name) | 2654 | 67,8 | [7 empty] | 35583 |  | 35583
|  | 8_A | 23769 | 347,8 | 25 x 2,5 | 0,96 | 0,31 | 83 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 8 | 23766 | 347,8 | 25 x 2,5 | 3,30 | 0,31 | 83 | 4,0 | 261 | 535 | 0 |  | 535 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 67 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1110
Circuit through Radiator: 203-1
Storey: 2 Second floor, Building unit: 08 , Room: 203 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 27 | 23834 | 348,5 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 269 | 486 | 0 |  | 486 | 25
|  | 27_A | 23796 | 348,5 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 2632 | 68,2 | [9 empty] | -743
| (Thermosiphon) | [12 empty] | 96
|  | 28 | 584 | 23,5 | 16 x 2,0 | 0,84 | 0,06 | 5 | 0,4 | 1 | 5 | 0 |  | 5 | 25
|  | 29 | 283 | 11,5 | 16 x 2,0 | 2,27 | 0,03 | 2 | 5,1 | 7 | 13 | 0 |  | 13 | 25
| Radiator | 203-1 | 254 | 11,5 | [7 empty] | 6510 |  | 6513
| Radiator (Thermosiphon) | [12 empty] | -21
|  | 30 | 283 | 11,5 | 16 x 2,0 | 2,11 | 0,03 | 3 | 5,5 | 7 | 14 | 0 |  | 14 | 25
|  | 28 | 584 | 23,5 | 16 x 2,0 | 0,80 | 0,06 | 7 | 0,8 | 1 | 7 | 0 |  | 7 | 25
| Flat station | (no name) | 2632 | 68,2 | [7 empty] | 33628 |  | 33628
|  | 27_A | 23785 | 348,5 | 25 x 2,5 | 0,96 | 0,31 | 84 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 27 | 23782 | 348,5 | 25 x 2,5 | 3,30 | 0,31 | 84 | 4,0 | 262 | 537 | 0 |  | 537 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1110
Circuit through Radiator: 204-1
Storey: 2 Second floor, Building unit: 08 , Room: 204 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 68 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 4758 | 123,7 | [9 empty] | -670
| (Thermosiphon) | [12 empty] | 95
|  | 39 | 892 | 35,8 | 16 x 2,0 | 0,82 | 0,09 | 14 | 0,4 | 2 | 13 | 0 |  | 13 | 25
|  | 40 | 635 | 27,2 | 16 x 2,0 | 1,64 | 0,07 | 6 | 3,9 | 15 | 25 | 0 |  | 25 | 25
|  | 41 | 372 | 18,6 | 16 x 2,0 | 1,70 | 0,05 | 4 | 5,2 | 11 | 18 | 0 |  | 18 | 25
| Radiator | 204-1 | 350 | 18,6 | [7 empty] | 17730 |  | 17737
| Radiator (Thermosiphon) | [12 empty] | -18
|  | 41 | 372 | 18,6 | 16 x 2,0 | 1,67 | 0,05 | 5 | 5,2 | 11 | 19 | 0 |  | 19 | 25
|  | 40 | 635 | 27,2 | 16 x 2,0 | 1,75 | 0,07 | 8 | 3,9 | 15 | 29 | 0 |  | 29 | 25
|  | 39 | 892 | 35,8 | 16 x 2,0 | 0,79 | 0,09 | 10 | 0,4 | 2 | 10 | 0 |  | 10 | 25
| Flat station | (no name) | 4758 | 123,7 | [7 empty] | 24667 |  | 24667
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1084
Circuit through Flat station: (no name)
Storey: 2 Second floor
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 18 | 24408 | 339,0 | 25 x 2,5 | 3,30 | 0,31 | 63 | 4,3 | 263 | 470 | 0 |  | 470 | 25
|  | 18_A | 24370 | 339,0 | 25 x 2,5 | 0,96 | 0,31 | 63 | 0,8 | 37 | 97 | 0 |  | 97 | 25
| Flat station | (no name) | 24757 | 339,0 | [9 empty] | 40270
|  | 18_A | 24359 | 339,0 | 25 x 2,5 | 0,96 | 0,30 | 81 | 0,8 | 36 | 114 | 0 |  | 114 | 25
|  | 18 | 24354 | 339,0 | 25 x 2,5 | 3,30 | 0,30 | 81 | 4,3 | 256 | 524 | 0 |  | 524 | 25
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 69 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1131
Circuit through Flat station: (no name)
Storey: 2 Second floor
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 8 | 23818 | 347,8 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 268 | 484 | 0 |  | 484 | 25
|  | 8_A | 23780 | 347,8 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 23335 | 347,8 | [9 empty] | 41441
|  | 8_A | 23769 | 347,8 | 25 x 2,5 | 0,96 | 0,31 | 83 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 8 | 23766 | 347,8 | 25 x 2,5 | 3,30 | 0,31 | 83 | 4,0 | 261 | 535 | 0 |  | 535 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1110
Circuit through Flat station: (no name)
Storey: 2 Second floor
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 27 | 23834 | 348,5 | 25 x 2,5 | 3,30 | 0,32 | 66 | 4,0 | 269 | 486 | 0 |  | 486 | 25
|  | 27_A | 23796 | 348,5 | 25 x 2,5 | 0,96 | 0,32 | 66 | 0,8 | 39 | 102 | 0 |  | 102 | 25
| Flat station | (no name) | 23335 | 348,5 | [9 empty] | 39511
|  | 27_A | 23785 | 348,5 | 25 x 2,5 | 0,96 | 0,31 | 84 | 0,8 | 38 | 118 | 0 |  | 118 | 25
|  | 27 | 23782 | 348,5 | 25 x 2,5 | 3,30 | 0,31 | 84 | 4,0 | 262 | 537 | 0 |  | 537 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 70 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1110
Circuit through Flat station: (no name)
Storey: 2 Second floor
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 38 | 46160 | 720,3 | 32 x 3,0 | 3,30 | 0,39 | 68 | 4,0 | 394 | 617 | 0 |  | 617 | 40
|  | 38_A | 46125 | 720,3 | 32 x 3,0 | 3,71 | 0,39 | 68 | 6,0 | 437 | 689 | 0 |  | 689 | 40
| Flat station | (no name) | 46708 | 720,3 | [9 empty] | 41924
|  | 38_A | 46089 | 720,3 | 32 x 3,0 | 3,71 | 0,38 | 84 | 6,0 | 426 | 736 | 0 |  | 736 | 40
|  | 38 | 46088 | 720,3 | 32 x 3,0 | 3,30 | 0,38 | 84 | 4,0 | 383 | 659 | 0 |  | 659 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 1084
Circuit through Radiator: 112-1
Storey: 1 First floor, Building unit: 02 , Room: 112 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -126
|  | 15 | 649 | 27,2 | 16 x 2,0 | 0,78 | 0,07 | 6 | 4,1 | 9 | 14 | 0 |  | 14 | 25
| (Thermosiphon) | [12 empty] | 93
|  | 15_A | 643 | 27,2 | 16 x 2,0 | 1,48 | 0,07 | 6 | 0,0 | 0 | 9 | 0 |  | 9 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 71 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 17 | 252 | 8,6 | 16 x 2,0 | 1,27 | 0,02 | 2 | 4,7 | 3 | 5 | 0 |  | 5 | 25
|  | 17_A | 241 | 8,6 | 16 x 2,0 | 3,14 | 0,02 | 2 | 1,2 | 0 | 6 | 0 |  | 6 | 25
| Radiator | 112-1 | 197 | 8,6 | [7 empty] | 11228 |  | 11228
| Radiator (Thermosiphon) | [12 empty] | -125
|  | 17 | 241 | 8,6 | 16 x 2,0 | 4,45 | 0,02 | 3 | 2,6 | 3 | 14 | 0 |  | 14 | 25
|  | 15_A | 643 | 27,2 | 16 x 2,0 | 1,49 | 0,07 | 8 | 0,0 | 0 | 11 | 0 |  | 11 | 25
|  | 15 | 647 | 27,2 | 16 x 2,0 | 0,82 | 0,07 | 8 | 4,1 | 9 | 16 | 0 |  | 16 | 25
| Flat station | (no name) | 4922 | 152,9 | [7 empty] | 28431 |  | 28431
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 475
Circuit through Radiator: 115-1
Storey: 1 First floor, Building unit: 02 , Room: 115 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 23 | 33353 | 501,8 | 25 x 2,5 | 0,96 | 0,46 | 125 | 3,9 | 396 | 515 | 0 |  | 515 | 25
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | -147
| (Thermosiphon) | [12 empty] | 97
|  | 24 | 586 | 23,5 | 16 x 2,0 | 0,84 | 0,06 | 5 | 0,4 | 1 | 5 | 0 |  | 5 | 25
|  | 26 | 291 | 11,9 | 16 x 2,0 | 5,58 | 0,03 | 3 | 5,1 | 7 | 21 | 0 |  | 21 | 25
| Radiator | 115-1 | 217 | 11,9 | [7 empty] | 12316 |  | 12316
| Radiator (Thermosiphon) | [12 empty] | -121
|  | 25 | 291 | 11,9 | 16 x 2,0 | 5,69 | 0,03 | 3 | 5,1 | 7 | 26 | 0 |  | 26 | 25
|  | 24 | 586 | 23,5 | 16 x 2,0 | 0,80 | 0,06 | 7 | 0,8 | 1 | 7 | 0 |  | 7 | 25
| Flat station | (no name) | 2633 | 81,2 | [7 empty] | 26858 |  | 26858
|  | 23 | 33343 | 501,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 385 | 535 | 0 |  | 535 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 72 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 467
Circuit through Radiator: 116-1
Storey: 1 First floor, Building unit: 02 , Room: 116 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 4 | 33332 | 500,8 | 25 x 2,5 | 0,96 | 0,45 | 125 | 3,9 | 394 | 514 | 0 |  | 514 | 25
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | -148
| (Thermosiphon) | [12 empty] | 97
|  | 5 | 581 | 23,5 | 16 x 2,0 | 0,80 | 0,06 | 5 | 0,8 | 1 | 5 | 0 |  | 5 | 25
|  | 7 | 286 | 11,9 | 16 x 2,0 | 5,11 | 0,03 | 3 | 5,1 | 7 | 20 | 0 |  | 20 | 25
| Radiator | 116-1 | 219 | 11,9 | [7 empty] | 12272 |  | 12272
| Radiator (Thermosiphon) | [12 empty] | -120
|  | 6 | 286 | 11,9 | 16 x 2,0 | 5,05 | 0,03 | 3 | 5,1 | 7 | 24 | 0 |  | 24 | 25
|  | 5 | 581 | 23,5 | 16 x 2,0 | 0,84 | 0,06 | 7 | 0,4 | 1 | 6 | 0 |  | 6 | 25
| Flat station | (no name) | 2655 | 80,5 | [7 empty] | 28833 |  | 28833
|  | 4 | 33322 | 500,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 384 | 533 | 0 |  | 533 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 468
Circuit through Radiator: 109-1
Storey: 1 First floor, Building unit: 02 , Room: 109 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -91
| (Thermosiphon) | [12 empty] | 96
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 73 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 33 | 893 | 35,8 | 16 x 2,0 | 0,82 | 0,09 | 14 | 0,4 | 2 | 13 | 0 |  | 13 | 25
|  | 37 | 247 | 8,6 | 16 x 2,0 | 3,52 | 0,02 | 2 | 5,5 | 16 | 22 | 0 |  | 22 | 25
| Radiator | 109-1 | 203 | 8,6 | [7 empty] | 25125 |  | 25125
| Radiator (Thermosiphon) | [12 empty] | -133
|  | 37 | 247 | 8,6 | 16 x 2,0 | 3,52 | 0,02 | 3 | 5,5 | 16 | 25 | 0 |  | 25 | 25
|  | 33 | 893 | 35,8 | 16 x 2,0 | 0,79 | 0,09 | 10 | 0,4 | 2 | 10 | 0 |  | 10 | 25
| Flat station | (no name) | 4706 | 144,1 | [7 empty] | 16351 |  | 16351
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 458
Circuit through Radiator: 111-1
Storey: 1 First floor, Building unit: 02 , Room: 111 Bathroom
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -91
| (Thermosiphon) | [12 empty] | 96
|  | 33 | 893 | 35,8 | 16 x 2,0 | 0,82 | 0,09 | 14 | 0,4 | 2 | 13 | 0 |  | 13 | 25
|  | 34 | 636 | 27,2 | 16 x 2,0 | 1,64 | 0,07 | 6 | 3,9 | 15 | 25 | 0 |  | 25 | 25
|  | 36 | 240 | 8,6 | 16 x 2,0 | 3,10 | 0,02 | 2 | 2,6 | 3 | 8 | 0 |  | 8 | 25
| Radiator | 111-1 | 202 | 8,6 | [7 empty] | 25093 |  | 25093
| Radiator (Thermosiphon) | [12 empty] | -127
|  | 36 | 240 | 8,6 | 16 x 2,0 | 2,97 | 0,02 | 3 | 2,6 | 3 | 10 | 0 |  | 10 | 25
|  | 34 | 636 | 27,2 | 16 x 2,0 | 1,75 | 0,07 | 8 | 3,9 | 15 | 29 | 0 |  | 29 | 25
|  | 33 | 893 | 35,8 | 16 x 2,0 | 0,79 | 0,09 | 10 | 0,4 | 2 | 10 | 0 |  | 10 | 25
| Flat station | (no name) | 4706 | 144,1 | [7 empty] | 16351 |  | 16351
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 458
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 74 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
Circuit through Radiator: 101-1
Storey: 1 First floor, Building unit: 02 , Room: 101 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 4922 | 152,9 | [9 empty] | -126
|  | 15 | 649 | 27,2 | 16 x 2,0 | 0,78 | 0,07 | 6 | 4,1 | 9 | 14 | 0 |  | 14 | 25
| (Thermosiphon) | [12 empty] | 93
|  | 15_A | 643 | 27,2 | 16 x 2,0 | 1,48 | 0,07 | 6 | 0,0 | 0 | 9 | 0 |  | 9 | 25
|  | 16 | 371 | 18,6 | 16 x 2,0 | 1,55 | 0,05 | 4 | 5,2 | 11 | 17 | 0 |  | 17 | 25
| Radiator | 101-1 | 350 | 18,6 | [7 empty] | 11103 |  | 11110
| Radiator (Thermosiphon) | [12 empty] | -18
|  | 16 | 371 | 18,6 | 16 x 2,0 | 1,70 | 0,05 | 5 | 5,2 | 11 | 19 | 0 |  | 19 | 25
|  | 15_A | 643 | 27,2 | 16 x 2,0 | 1,49 | 0,07 | 8 | 0,0 | 0 | 11 | 0 |  | 11 | 25
|  | 15 | 647 | 27,2 | 16 x 2,0 | 0,82 | 0,07 | 8 | 4,1 | 9 | 16 | 0 |  | 16 | 25
| Flat station | (no name) | 4922 | 152,9 | [7 empty] | 28431 |  | 28431
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 475
Circuit through Radiator: 103-1
Storey: 1 First floor, Building unit: 02 , Room: 103 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 23 | 33353 | 501,8 | 25 x 2,5 | 0,96 | 0,46 | 125 | 3,9 | 396 | 515 | 0 |  | 515 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 75 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Flat station | (no name) | 2633 | 81,2 | [9 empty] | -147
| (Thermosiphon) | [12 empty] | 97
|  | 24 | 586 | 23,5 | 16 x 2,0 | 0,84 | 0,06 | 5 | 0,4 | 1 | 5 | 0 |  | 5 | 25
|  | 25 | 283 | 11,5 | 16 x 2,0 | 2,27 | 0,03 | 2 | 5,1 | 7 | 13 | 0 |  | 13 | 25
| Radiator | 103-1 | 255 | 11,5 | [7 empty] | 12233 |  | 12236
| Radiator (Thermosiphon) | [12 empty] | -21
|  | 26 | 283 | 11,5 | 16 x 2,0 | 2,11 | 0,03 | 3 | 5,5 | 7 | 14 | 0 |  | 14 | 25
|  | 24 | 586 | 23,5 | 16 x 2,0 | 0,80 | 0,06 | 7 | 0,8 | 1 | 7 | 0 |  | 7 | 25
| Flat station | (no name) | 2633 | 81,2 | [7 empty] | 26858 |  | 26858
|  | 23 | 33343 | 501,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 385 | 535 | 0 |  | 535 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 467
Circuit through Radiator: 106-1
Storey: 1 First floor, Building unit: 02 , Room: 106 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 4 | 33332 | 500,8 | 25 x 2,5 | 0,96 | 0,45 | 125 | 3,9 | 394 | 514 | 0 |  | 514 | 25
| Flat station | (no name) | 2655 | 80,5 | [9 empty] | -148
| (Thermosiphon) | [12 empty] | 97
|  | 5 | 581 | 23,5 | 16 x 2,0 | 0,80 | 0,06 | 5 | 0,8 | 1 | 5 | 0 |  | 5 | 25
|  | 6 | 284 | 11,5 | 16 x 2,0 | 2,13 | 0,03 | 2 | 5,5 | 7 | 13 | 0 |  | 13 | 25
| Radiator | 106-1 | 256 | 11,5 | [7 empty] | 12187 |  | 12189
| Radiator (Thermosiphon) | [12 empty] | -21
|  | 7 | 284 | 11,5 | 16 x 2,0 | 2,23 | 0,03 | 3 | 5,1 | 7 | 14 | 0 |  | 14 | 25
|  | 5 | 581 | 23,5 | 16 x 2,0 | 0,84 | 0,06 | 7 | 0,4 | 1 | 6 | 0 |  | 6 | 25
| Flat station | (no name) | 2655 | 80,5 | [7 empty] | 28833 |  | 28833
|  | 4 | 33322 | 500,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 384 | 533 | 0 |  | 533 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 76 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 468
Circuit through Radiator: 104-1
Storey: 1 First floor, Building unit: 02 , Room: 104 Living room
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 4706 | 144,1 | [9 empty] | -91
| (Thermosiphon) | [12 empty] | 96
|  | 33 | 893 | 35,8 | 16 x 2,0 | 0,82 | 0,09 | 14 | 0,4 | 2 | 13 | 0 |  | 13 | 25
|  | 34 | 636 | 27,2 | 16 x 2,0 | 1,64 | 0,07 | 6 | 3,9 | 15 | 25 | 0 |  | 25 | 25
|  | 35 | 372 | 18,6 | 16 x 2,0 | 1,70 | 0,05 | 4 | 5,2 | 11 | 18 | 0 |  | 18 | 25
| Radiator | 104-1 | 350 | 18,6 | [7 empty] | 24960 |  | 24967
| Radiator (Thermosiphon) | [12 empty] | -18
|  | 35 | 372 | 18,6 | 16 x 2,0 | 1,67 | 0,05 | 5 | 5,2 | 11 | 19 | 0 |  | 19 | 25
|  | 34 | 636 | 27,2 | 16 x 2,0 | 1,75 | 0,07 | 8 | 3,9 | 15 | 29 | 0 |  | 29 | 25
|  | 33 | 893 | 35,8 | 16 x 2,0 | 0,79 | 0,09 | 10 | 0,4 | 2 | 10 | 0 |  | 10 | 25
| Flat station | (no name) | 4706 | 144,1 | [7 empty] | 16351 |  | 16351
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 458
Circuit through Flat station: (no name)
Storey: 1 First floor
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 13 | 69983 | 994,6 | 32 x 3,0 | 0,58 | 0,53 | 120 | 5,2 | 653 | 722 | 0 |  | 722 | 40
| (Thermosiphon) | [12 empty] | -39
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,53 | 120 | 0,0 | 0 | 47 | 0 |  | 47 | 40
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 77 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
|  | 14 | 45572 | 655,6 | 32 x 3,0 | 0,96 | 0,35 | 57 | 6,0 | 567 | 622 | 0 |  | 622 | 40
| Flat station | (no name) | 46708 | 655,6 | [9 empty] | 39576
|  | 14 | 45561 | 655,6 | 32 x 3,0 | 0,96 | 0,34 | 73 | 6,0 | 551 | 621 | 0 |  | 621 | 40
|  | 13_A | 69977 | 994,6 | 32 x 3,0 | 0,39 | 0,52 | 152 | 0,0 | 0 | 60 | 0 |  | 60 | 40
|  | 13 | 69976 | 994,6 | 32 x 3,0 | 0,74 | 0,52 | 152 | 5,2 | 635 | 748 | 0 |  | 748 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 475
Circuit through Flat station: (no name)
Storey: 1 First floor
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 3 | 57193 | 848,6 | 32 x 3,0 | 4,08 | 0,46 | 91 | 5,2 | 851 | 1221 | 0 |  | 1221 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 35 | 0 |  | 35 | 40
|  | 4 | 33332 | 500,8 | 25 x 2,5 | 0,96 | 0,45 | 125 | 3,9 | 394 | 514 | 0 |  | 514 | 25
| Flat station | (no name) | 33468 | 500,8 | [9 empty] | 40990
|  | 4 | 33322 | 500,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 384 | 533 | 0 |  | 533 | 25
|  | 3_A | 57150 | 848,6 | 32 x 3,0 | 0,39 | 0,44 | 113 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 3 | 57148 | 848,6 | 32 x 3,0 | 3,92 | 0,44 | 113 | 5,2 | 829 | 1273 | 0 |  | 1273 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 468
Circuit through Flat station: (no name)
Storey: 1 First floor
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,38 | 0,68 | 143 | 2,6 | 407 | 749 | 0 |  | 749 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,36 | 0,48 | 77 | 1,4 | 317 | 1036 | 0 |  | 1036 | 40
|  | 22 | 57231 | 850,3 | 32 x 3,0 | 0,06 | 0,46 | 91 | 4,0 | 421 | 427 | 0 |  | 427 | 40
|  | 22_A | 57230 | 850,3 | 32 x 3,0 | 4,08 | 0,46 | 91 | 2,6 | 264 | 635 | 0 |  | 635 | 40
| (Thermosiphon) | [12 empty] | -38
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,46 | 91 | 0,0 | 0 | 36 | 0 |  | 36 | 40
|  | 23 | 33353 | 501,8 | 25 x 2,5 | 0,96 | 0,46 | 125 | 3,9 | 396 | 515 | 0 |  | 515 | 25
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 78 -
Project:
Description |  | Symbol | Φ | m | Diam. | L | v | R | ζ | Z | R*L+Z | Press. drop. fitt. |  | Tot. press. drop | Insul.
|  |  | W | kg/h | mm | m | m/s | Pa/m |  | Pa | Pa | Pa |  | Pa | mm
| Flat station | (no name) | 33468 | 501,8 | [9 empty] | 39062
|  | 23 | 33343 | 501,8 | 25 x 2,5 | 0,96 | 0,44 | 156 | 3,9 | 385 | 535 | 0 |  | 535 | 25
|  | 22_B | 57187 | 850,3 | 32 x 3,0 | 0,39 | 0,44 | 114 | 0,0 | 0 | 44 | 0 |  | 44 | 40
|  | 22_A | 57185 | 850,3 | 32 x 3,0 | 3,92 | 0,44 | 114 | 2,6 | 257 | 703 | 0 |  | 703 | 40
|  | 22 | 57185 | 850,3 | 32 x 3,0 | 0,17 | 0,44 | 114 | 4,0 | 410 | 429 | 0 |  | 429 | 40
|  | 12 | 88594 | 1353,5 | 40 x 4,0 | 9,25 | 0,47 | 95 | 1,4 | 308 | 1187 | 0 |  | 1187 | 40
|  | 2 | 125364 | 1922,2 | 40 x 4,0 | 2,33 | 0,66 | 176 | 2,6 | 396 | 807 | 0 |  | 807 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 467
Circuit through Flat station: (no name)
Storey: 1 First floor
| Source | 1 | 163413 | 2624,3 | [9 empty] | 0
| Source (H avail.) | [12 empty] | -35281
|  | 1 | 164753 | 2624,3 | 50 x 4,5 | 0,23 | 0,57 | 76 | 2,9 | 454 | 472 | 0 |  | 472 | 50
| (Thermosiphon) | [12 empty] | -234
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,53 | 0,57 | 76 | 2,1 | 329 | 522 | 0 |  | 522 | 50
|  | 31 | 97957 | 1543,0 | 40 x 4,0 | 0,45 | 0,55 | 97 | 4,4 | 656 | 700 | 0 |  | 700 | 40
|  | 31_A | 97951 | 1543,0 | 40 x 4,0 | 0,22 | 0,55 | 97 | 2,1 | 306 | 328 | 0 |  | 328 | 40
| (Thermosiphon) | [12 empty] | -37
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,55 | 97 | 0,0 | 0 | 38 | 0 |  | 38 | 40
|  | 32 | 51783 | 822,8 | 32 x 3,0 | 3,71 | 0,44 | 86 | 8,6 | 950 | 1268 | 0 |  | 1268 | 40
| Flat station | (no name) | 52758 | 822,8 | [9 empty] | 41416
|  | 32 | 51747 | 822,8 | 32 x 3,0 | 3,71 | 0,43 | 105 | 8,6 | 925 | 1315 | 0 |  | 1315 | 40
|  | 31_B | 97949 | 1543,0 | 40 x 4,0 | 0,39 | 0,53 | 118 | 0,0 | 0 | 46 | 0 |  | 46 | 40
|  | 31_A | 97949 | 1543,0 | 40 x 4,0 | 0,32 | 0,53 | 118 | 2,1 | 298 | 336 | 0 |  | 336 | 40
|  | 31 | 97949 | 1543,0 | 40 x 4,0 | 0,56 | 0,53 | 118 | 4,4 | 640 | 706 | 0 |  | 706 | 40
|  | 1_A | 164750 | 2624,3 | 50 x 4,5 | 2,27 | 0,55 | 92 | 2,1 | 320 | 530 | 0 |  | 530 | 50
|  | 1 | 164750 | 2624,3 | 50 x 4,5 | 0,33 | 0,55 | 92 | 4,1 | 625 | 656 | 0 |  | 656 | 50
| Pump | (no name) |  | 2624,3 | [9 empty] | -12323
[12 empty] | Total: |  | 458
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [12 empty] | - 79 -

## List of pipes, pipe fitting
Project:
List of pipes, pipe fittings and couplings
Product |  | Size |  |  | Catalogue code |  | Qty. | Unit
Brass and steel pipe couplings and fittings
Pipe fittings
| Female connector, reduction, imperial | 1¾"FT - 1½"FT |  |  |  |  | 2 | pcs.
| Female connector, straight, imperial | 1½"FT - 1½"FT |  |  |  |  | 1 | pcs.
| Nipple, reduction, imperial | 1"MT - ¾"MT |  |  |  |  | 6 | pcs.
PEX/AL/PE-RT System (pipes and fittings)
Pipes
| Pipe PE-X/AL/PE-RT in coils | 16 x 2,0 |  |  |  |  | 144 | m
| Pipe PE-X/AL/PE-RT in coils | 25 x 2,5 |  |  |  |  | 30 | m
| Pipe PE-X/AL/PE-RT in straight lenghts | 32 x 3,0 |  |  |  |  | 44 | m
| Pipe PE-X/AL/PE-RT in straight lenghts | 40 x 4,0 |  |  |  |  | 26 | m
| Pipe PE-X/AL/PE-RT in straight lenghts | 50 x 4,5 |  |  |  |  | 6 | m
Pipe fittings
| Connection adapter with ring | 16 - ¾"FT |  |  |  |  | 36 | pcs.
| Coupling | 40 - 40 |  |  |  |  | 2 | pcs.
| Coupling FT | 32 - 1"FT |  |  |  |  | 6 | pcs.
| Coupling MT | 25 - ¾"MT |  |  |  |  | 10 | pcs.
| Coupling MT | 50 - 1½"MT |  |  |  |  | 4 | pcs.
| Elbow 90° | 16 - 16 |  |  |  |  | 6 | pcs.
| Elbow 90° | 25 - 25 |  |  |  |  | 6 | pcs.
| Elbow 90° | 32 - 32 |  |  |  |  | 20 | pcs.
| Elbow 90° | 40 - 40 |  |  |  |  | 4 | pcs.
| Elbow 90° | 50 - 50 |  |  |  |  | 4 | pcs.
| Reduction | 32 - 25 |  |  |  |  | 2 | pcs.
| Reduction | 50 - 40 |  |  |  |  | 2 | pcs.
| Tee | 16 - 16 - 16 |  |  |  |  | 20 | pcs.
| Tee | 32 - 32 - 32 |  |  |  |  | 2 | pcs.
| Tee | 32 - 25 - 25 |  |  |  |  | 4 | pcs.
| Tee | 40 - 32 - 32 |  |  |  |  | 4 | pcs.
| Tee | 40 - 32 - 40 |  |  |  |  | 2 | pcs.
| Tee | 50 - 40 - 50 |  |  |  |  | 2 | pcs.
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 80 -
Project:
List of insulation
Product |  | Size |  |  | Catalogue code |  | Qty. | Unit
Standard insulation catalogue
Lagging
| PU foam lagging, λ(20°C)=0,036W/mK | Int. diam. = 18 mm. Thickness = 25 mm |  |  |  |  | 144 | m
| PU foam lagging, λ(20°C)=0,036W/mK | Int. diam. = 25 mm. Thickness = 25 mm |  |  |  |  | 30 | m
| PU foam lagging, λ(20°C)=0,036W/mK | Int. diam. = 35 mm. Thickness = 40 mm |  |  |  |  | 44 | m
| PU foam lagging, λ(20°C)=0,036W/mK | Int. diam. = 42 mm. Thickness = 40 mm |  |  |  |  | 26 | m
| PU foam lagging, λ(20°C)=0,036W/mK | Int. diam. = 54 mm. Thickness = 50 mm |  |  |  |  | 6 | m
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 81 -
Project:
List of valves and fittings
Product |  | Size |  |  | Catalogue code |  | Qty. | Unit
Items not from catalogues
Pumps
| Pump: , H=12,3 kPa, V=0,7 dm³/s | [5 empty] | 1 | pcs.
Neutral valves catalogue - typical construction
Valves
| Valve connection, straight MT (2-p) | 15 |  |  |  |  | 8 | pcs.
VK - collective catalogue
Heads (thermostatic)/Actuators
| Thermostatic head for VK | [5 empty] | 18 | pcs.
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 82 -
Project:
List of radiators
Product |  | L | H | D | Catalogue code |  | Qty. | Unit
NEUTRAL RADIATORS
Neutral bathroom radiators VK
| BTHV_550_135 | 550 | 420 | 135 |  |  | 10 | pcs.
Neutral steel panel radiators VK (right side conn.)
| PLV11_450 | 400 | 450 | 60 |  |  | 4 | pcs.
| PLV11_600 | 400 | 600 | 60 |  |  | 4 | pcs.
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 83 -
Project:
List of flat stations
Product |  | Size |  |  | Catalogue code |  | Qty. | Unit
Flat stations - sample solutions
Flat stations
| Flat stations (for UFH and radiator systems) | Hot water demand: 10-12 l/min |  |  |  |  | 6 | pcs.
| Flat stations (for UFH and radiator systems) | Hot water demand: 15-17 l/min |  |  |  |  | 2 | pcs.
| Optional Sets | Heating circuit connection |  |  |  |  | 8 | pcs.
Manifolds
| Manifold with flowmeters | No.outlets: 4, conn.diam.: 1"FT , branch: ¾"MT |  |  | 4 |  | 4 | pcs.
| Manifold with flowmeters | No.outlets: 8, conn.diam.: 1"FT , branch: ¾"MT |  |  | 8 |  | 4 | pcs.
Cabinets
| On wall manifold cabinet | 580x1300x200 |  |  |  |  | 8 | pcs.
Neutral valves catalogue - typical construction
Valves
| Differential pressure regulator 10-60 kPa, FT | 20 |  |  |  |  | 7 | pcs.
| Differential pressure regulator 5-30 kPa, FT | 15 |  |  |  |  | 1 | pcs.
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [5 empty] | - 84 -

## Pipes summary
Project:
Pipes summary
Product | Size | Catalogue code | Insulated | Non-insulated | User specified | Sized | Under design |  | Existing | From radiant systems
|  |  | m | m | m | m | m |  | m | m
PEX pipe | 16x2.0 | any producer | [7 empty] | 2947,42
Pipe PE-X/AL/PE-RT in coils | 16 x 2,0 |  | 143,22 |  |  | 143,22 | 143,22
Pipe PE-X/AL/PE-RT in coils | 25 x 2,5 |  | 29,38 |  |  | 29,38 | 29,38
Pipe PE-X/AL/PE-RT in straight lenghts | 32 x 3,0 |  | 43,25 |  |  | 43,25 | 43,25
Pipe PE-X/AL/PE-RT in straight lenghts | 40 x 4,0 |  | 25,67 |  |  | 25,67 | 25,67
Pipe PE-X/AL/PE-RT in straight lenghts | 50 x 4,5 |  | 5,37 |  |  | 5,37 | 5,37
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [7 empty] | - 85 -

## General results - Water sup
Project:
General results - Water supply
No. of sources |  |  | 1
No. of heaters |  |  | 8
Circulation circuit |  |  | 0
Calculations made acc. to: |  |  | DIN 1988-300
| Name |  |  | In general | Hot water |  | Cold water |  |  | Circulation
| No. of receptors |  |  | 76 | 29 | 47
| Total number of pipe-runs |  |  | 233 | 78 | 155 |  |  | 0
| Total pipe network length [m] |  |  | 374,5 | 156,6 | 218,0 |  |  | 0,0
| Total capacity of pipe network [dm³] |  |  | 63,2 | 17,1 | 46,1 |  |  | 0,0
Results for particular water sources
Source
Source elevation |  | -1,5
Building type |  | Residential building
| Name |  |  | Hot water | Cold water |  | Circulation
| Available pressure [kPa] |  |  |  | 319,004
| Water temperature [ °C] |  |  |  | 10,0
| Flow rate at source [ dm³/s] |  |  |  | 1,260
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [7 empty] | - 86 -

## Cold water pipe-runs
Project:
Cold water pipe-runs
Pipe-run symbol |  | Sum of normative outputs | Calculation flow | Diameter | Length | Specific friction resistance | Flow velocity | Total friction loss | Pressure drop across fittings | Pressure drop in fittings | Total pressure drop |  | Insulation thickness
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
Source:
| 1 | 8,06 | 1,26 | 40 x 5,5 | 1,96 | 1355,52 | 1,91 | 4,05 | 7,369 | 0,000 | 10,019 |  | 0
| 2 | 5,26 | 1,09 | 40 x 5,5 | 2,34 | 1045,92 | 1,65 | 3,30 | 4,482 | 0,000 | 6,929 |  | 0
| 3 | 1,66 | 0,69 | 32 x 4,4 | 3,77 | 1350,71 | 1,63 | 4,95 | 6,584 | 0,000 | 11,681 |  | 0
| 3_A | 1,66 | 0,69 | 32 x 4,4 | 0,79 | 1350,65 | 1,63 | 0,25 | 0,333 | 0,000 | 1,401 |  | 0
| 4 | 0,86 | 0,50 | 25 x 3,5 | 0,56 | 2549,10 | 1,96 | 3,60 | 6,897 | 0,000 | 8,322 |  | 0
| 5 | 0,57 | 0,39 | 25 x 3,5 | 0,49 | 1654,95 | 1,53 | 0,00 | 0,000 | 0,000 | 0,815 |  | 0
| 6 | 0,07 | 0,07 | 16 x 2,2 | 1,26 | 655,81 | 0,66 | 0,00 | 0,000 | 0,000 | 0,828 |  | 0
| 7 | 0,50 | 0,36 | 25 x 3,5 | 2,57 | 1418,12 | 1,40 | 1,90 | 1,873 | 0,000 | 5,516 |  | 0
| 7_A | 0,50 | 0,36 | 25 x 3,5 | 0,94 | 1418,04 | 1,40 | 1,90 | 1,873 | 0,000 | 3,202 |  | 0
| 7_B | 0,50 | 0,36 | 25 x 3,5 | 2,17 | 1417,97 | 1,40 | 0,00 | 0,000 | 0,000 | 3,077 |  | 0
| 8 | 0,15 | 0,15 | 16 x 2,2 | 0,53 | 2491,38 | 1,42 | 0,00 | 0,000 | 0,000 | 1,326 |  | 0
| 9 | 0,35 | 0,27 | 20 x 2,8 | 0,76 | 2542,53 | 1,67 | 0,00 | 0,000 | 0,000 | 1,944 |  | 0
| 10 | 0,13 | 0,13 | 16 x 2,2 | 0,53 | 1937,89 | 1,23 | 0,00 | 0,000 | 0,000 | 1,032 |  | 0
| 11 | 0,22 | 0,17 | 16 x 2,2 | 3,45 | 3103,93 | 1,61 | 0,00 | 0,000 | 0,000 | 10,719 |  | 0
| 12 | 0,15 | 0,15 | 16 x 2,2 | 0,64 | 2490,89 | 1,42 | 0,00 | 0,000 | 0,000 | 1,583 |  | 0
| 13 | 0,07 | 0,07 | 16 x 2,2 | 0,84 | 655,57 | 0,66 | 0,00 | 0,000 | 0,000 | 0,549 |  | 0
| 13_A | 0,07 | 0,07 | 16 x 2,2 | 2,44 | 655,44 | 0,66 | 0,00 | 0,000 | 0,000 | 1,597 |  | 0
| 14 | 0,80 | 0,48 | 25 x 3,5 | 3,30 | 2374,23 | 1,88 | 4,10 | 7,248 | 0,000 | 15,083 |  | 0
| 14_A | 0,80 | 0,48 | 25 x 3,5 | 0,56 | 2374,12 | 1,88 | 0,00 | 0,000 | 0,000 | 1,327 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 87 -
Project:
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
| 15 | 0,59 | 0,40 | 25 x 3,5 | 0,49 | 1720,82 | 1,57 | 0,00 | 0,000 | 0,000 | 0,847 |  | 0
| 16 | 0,07 | 0,07 | 16 x 2,2 | 1,26 | 655,76 | 0,66 | 0,00 | 0,000 | 0,000 | 0,828 |  | 0
| 17 | 0,52 | 0,37 | 25 x 3,5 | 2,08 | 1486,60 | 1,44 | 0,80 | 0,832 | 0,000 | 3,919 |  | 0
| 18 | 0,25 | 0,25 | 20 x 2,8 | 0,56 | 2186,43 | 1,54 | 1,65 | 1,943 | 0,000 | 3,162 |  | 0
| 19 | 0,27 | 0,21 | 20 x 2,8 | 0,76 | 1663,66 | 1,31 | 2,20 | 1,899 | 0,000 | 3,172 |  | 0
| 20 | 0,13 | 0,13 | 16 x 2,2 | 0,53 | 1937,95 | 1,23 | 0,00 | 0,000 | 0,000 | 1,032 |  | 0
| 21 | 0,14 | 0,08 | 16 x 2,2 | 3,45 | 803,70 | 0,74 | 0,00 | 0,000 | 0,000 | 2,775 |  | 0
| 22 | 0,07 | 0,07 | 16 x 2,2 | 0,64 | 655,47 | 0,66 | 0,00 | 0,000 | 0,000 | 0,417 |  | 0
| 23 | 0,07 | 0,07 | 16 x 2,2 | 0,84 | 655,46 | 0,66 | 0,00 | 0,000 | 0,000 | 0,549 |  | 0
| 23_A | 0,07 | 0,07 | 16 x 2,2 | 2,44 | 655,33 | 0,66 | 0,00 | 0,000 | 0,000 | 1,596 |  | 0
| 24 | 3,60 | 0,95 | 40 x 5,5 | 9,42 | 817,97 | 1,43 | 1,90 | 1,956 | 0,000 | 9,663 |  | 0
| 25 | 1,66 | 0,69 | 32 x 4,4 | 3,77 | 1350,49 | 1,63 | 4,95 | 6,584 | 0,000 | 11,680 |  | 0
| 25_A | 1,66 | 0,69 | 32 x 4,4 | 0,79 | 1350,43 | 1,63 | 0,25 | 0,333 | 0,000 | 1,401 |  | 0
| 26 | 0,86 | 0,50 | 25 x 3,5 | 0,56 | 2548,69 | 1,96 | 3,60 | 6,897 | 0,000 | 8,322 |  | 0
| 27 | 0,57 | 0,39 | 25 x 3,5 | 0,46 | 1654,69 | 1,53 | 0,00 | 0,000 | 0,000 | 0,764 |  | 0
| 28 | 0,50 | 0,36 | 25 x 3,5 | 2,16 | 1417,90 | 1,40 | 1,90 | 1,873 | 0,000 | 4,934 |  | 0
| 28_A | 0,50 | 0,36 | 25 x 3,5 | 0,98 | 1417,83 | 1,40 | 1,90 | 1,873 | 0,000 | 3,267 |  | 0
| 28_B | 0,50 | 0,36 | 25 x 3,5 | 2,54 | 1417,75 | 1,40 | 0,00 | 0,000 | 0,000 | 3,607 |  | 0
| 29 | 0,15 | 0,15 | 16 x 2,2 | 0,50 | 2490,97 | 1,42 | 0,00 | 0,000 | 0,000 | 1,250 |  | 0
| 30 | 0,35 | 0,27 | 20 x 2,8 | 1,02 | 2542,10 | 1,67 | 0,00 | 0,000 | 0,000 | 2,596 |  | 0
| 31 | 0,13 | 0,13 | 16 x 2,2 | 0,50 | 1937,55 | 1,23 | 0,00 | 0,000 | 0,000 | 0,973 |  | 0
| 32 | 0,22 | 0,17 | 16 x 2,2 | 2,75 | 3103,44 | 1,61 | 0,00 | 0,000 | 0,000 | 8,521 |  | 0
| 33 | 0,15 | 0,15 | 16 x 2,2 | 0,56 | 2490,55 | 1,42 | 0,00 | 0,000 | 0,000 | 1,386 |  | 0
| 34 | 0,07 | 0,07 | 16 x 2,2 | 3,13 | 655,38 | 0,66 | 0,00 | 0,000 | 0,000 | 2,051 |  | 0
| 35 | 0,07 | 0,07 | 16 x 2,2 | 1,73 | 655,68 | 0,66 | 0,00 | 0,000 | 0,000 | 1,137 |  | 0
| 36 | 0,80 | 0,48 | 25 x 3,5 | 3,30 | 2373,85 | 1,88 | 4,10 | 7,248 | 0,000 | 15,082 |  | 0
| 36_A | 0,80 | 0,48 | 25 x 3,5 | 0,56 | 2373,74 | 1,88 | 0,00 | 0,000 | 0,000 | 1,327 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 88 -
Project:
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
| 37 | 0,59 | 0,40 | 25 x 3,5 | 0,46 | 1720,54 | 1,57 | 0,00 | 0,000 | 0,000 | 0,795 |  | 0
| 38 | 0,52 | 0,37 | 25 x 3,5 | 2,09 | 1486,36 | 1,44 | 0,80 | 0,832 | 0,000 | 3,934 |  | 0
| 39 | 0,25 | 0,25 | 20 x 2,8 | 0,53 | 2186,08 | 1,54 | 1,65 | 1,943 | 0,000 | 3,095 |  | 0
| 40 | 0,27 | 0,21 | 20 x 2,8 | 1,02 | 1663,37 | 1,31 | 2,20 | 1,899 | 0,000 | 3,598 |  | 0
| 41 | 0,13 | 0,13 | 16 x 2,2 | 0,50 | 1937,60 | 1,23 | 0,00 | 0,000 | 0,000 | 0,973 |  | 0
| 42 | 0,14 | 0,08 | 16 x 2,2 | 2,75 | 803,58 | 0,74 | 0,00 | 0,000 | 0,000 | 2,206 |  | 0
| 43 | 0,07 | 0,07 | 16 x 2,2 | 0,56 | 655,40 | 0,66 | 0,00 | 0,000 | 0,000 | 0,365 |  | 0
| 44 | 0,07 | 0,07 | 16 x 2,2 | 3,13 | 655,30 | 0,66 | 0,00 | 0,000 | 0,000 | 2,050 |  | 0
| 45 | 0,07 | 0,07 | 16 x 2,2 | 1,73 | 655,62 | 0,66 | 0,00 | 0,000 | 0,000 | 1,137 |  | 0
| 46 | 1,94 | 0,74 | 32 x 4,4 | 0,17 | 1524,88 | 1,75 | 3,55 | 5,417 | 0,000 | 5,683 |  | 0
| 46_A | 1,94 | 0,74 | 32 x 4,4 | 0,88 | 1524,87 | 1,75 | 1,90 | 2,899 | 0,000 | 4,238 |  | 0
| 46_B | 1,94 | 0,74 | 32 x 4,4 | 0,79 | 1524,85 | 1,75 | 0,25 | 0,381 | 0,000 | 1,588 |  | 0
| 47 | 1,37 | 0,63 | 32 x 4,4 | 0,56 | 1154,97 | 1,49 | 3,05 | 3,399 | 0,000 | 4,046 |  | 0
| 48 | 0,94 | 0,52 | 32 x 4,4 | 0,46 | 827,72 | 1,24 | 0,25 | 0,191 | 0,000 | 0,571 |  | 0
| 49 | 0,35 | 0,27 | 20 x 2,8 | 0,74 | 2542,73 | 1,67 | 3,55 | 4,963 | 0,000 | 6,833 |  | 0
| 49_A | 0,35 | 0,27 | 20 x 2,8 | 2,82 | 2542,57 | 1,67 | 1,90 | 2,656 | 0,000 | 9,816 |  | 0
| 49_B | 0,35 | 0,27 | 20 x 2,8 | 5,49 | 2542,20 | 1,67 | 0,00 | 0,000 | 0,000 | 13,944 |  | 0
| 50 | 0,15 | 0,15 | 16 x 2,2 | 0,84 | 2490,75 | 1,42 | 0,00 | 0,000 | 0,000 | 2,098 |  | 0
| 51 | 0,20 | 0,15 | 16 x 2,2 | 0,81 | 2493,02 | 1,42 | 0,00 | 0,000 | 0,000 | 2,026 |  | 0
| 52 | 0,07 | 0,07 | 16 x 2,2 | 0,74 | 655,51 | 0,66 | 0,00 | 0,000 | 0,000 | 0,487 |  | 0
| 53 | 0,13 | 0,13 | 16 x 2,2 | 0,81 | 1937,36 | 1,23 | 0,00 | 0,000 | 0,000 | 1,566 |  | 0
| 54 | 0,59 | 0,40 | 25 x 3,5 | 0,77 | 1720,75 | 1,57 | 3,00 | 3,683 | 0,000 | 5,007 |  | 0
| 55 | 0,25 | 0,25 | 20 x 2,8 | 0,50 | 2186,47 | 1,54 | 1,65 | 1,943 | 0,000 | 3,033 |  | 0
| 56 | 0,34 | 0,27 | 20 x 2,8 | 0,68 | 2434,18 | 1,63 | 2,20 | 2,927 | 0,000 | 4,574 |  | 0
| 57 | 0,13 | 0,13 | 16 x 2,2 | 0,50 | 1938,01 | 1,23 | 0,00 | 0,000 | 0,000 | 0,969 |  | 0
| 58 | 0,21 | 0,16 | 16 x 2,2 | 1,13 | 2797,61 | 1,52 | 0,00 | 0,000 | 0,000 | 3,154 |  | 0
| 58_A | 0,21 | 0,16 | 16 x 2,2 | 1,41 | 2797,43 | 1,52 | 0,00 | 0,000 | 0,000 | 3,956 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 89 -
Project:
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
| 59 | 0,07 | 0,07 | 16 x 2,2 | 0,57 | 655,65 | 0,66 | 0,00 | 0,000 | 0,000 | 0,371 |  | 0
| 60 | 0,14 | 0,08 | 16 x 2,2 | 2,32 | 803,66 | 0,74 | 0,00 | 0,000 | 0,000 | 1,866 |  | 0
| 61 | 0,07 | 0,07 | 16 x 2,2 | 0,73 | 655,47 | 0,66 | 0,00 | 0,000 | 0,000 | 0,481 |  | 0
| 62 | 0,07 | 0,07 | 16 x 2,2 | 1,72 | 655,44 | 0,66 | 0,00 | 0,000 | 0,000 | 1,130 |  | 0
| 62_A | 0,07 | 0,07 | 16 x 2,2 | 2,78 | 655,26 | 0,66 | 0,00 | 0,000 | 0,000 | 1,823 |  | 0
| 62_B | 0,07 | 0,07 | 16 x 2,2 | 6,72 | 654,89 | 0,66 | 0,00 | 0,000 | 0,000 | 4,400 |  | 0
| 62_C | 0,07 | 0,07 | 16 x 2,2 | 1,87 | 654,55 | 0,66 | 0,00 | 0,000 | 0,000 | 1,223 |  | 0
| 63 | 0,57 | 0,39 | 25 x 3,5 | 3,30 | 1654,73 | 1,53 | 4,10 | 4,816 | 0,000 | 10,276 |  | 0
| 63_A | 0,57 | 0,39 | 25 x 3,5 | 0,56 | 1654,64 | 1,53 | 0,00 | 0,000 | 0,000 | 0,926 |  | 0
| 64 | 0,35 | 0,27 | 20 x 2,8 | 0,46 | 2542,51 | 1,67 | 1,90 | 2,656 | 0,000 | 3,822 |  | 0
| 64_A | 0,35 | 0,27 | 20 x 2,8 | 5,44 | 2542,25 | 1,67 | 0,00 | 0,000 | 0,000 | 13,821 |  | 0
| 65 | 0,15 | 0,15 | 16 x 2,2 | 0,84 | 2490,81 | 1,42 | 0,00 | 0,000 | 0,000 | 2,098 |  | 0
| 66 | 0,20 | 0,15 | 16 x 2,2 | 0,81 | 2493,07 | 1,42 | 0,00 | 0,000 | 0,000 | 2,026 |  | 0
| 67 | 0,07 | 0,07 | 16 x 2,2 | 0,74 | 655,52 | 0,66 | 0,00 | 0,000 | 0,000 | 0,487 |  | 0
| 68 | 0,13 | 0,13 | 16 x 2,2 | 0,81 | 1937,40 | 1,23 | 0,00 | 0,000 | 0,000 | 1,566 |  | 0
| 69 | 2,80 | 0,86 | 40 x 5,5 | 0,73 | 688,46 | 1,30 | 5,45 | 4,616 | 0,000 | 5,115 |  | 0
| 69_A | 2,80 | 0,86 | 40 x 5,5 | 0,79 | 688,45 | 1,30 | 0,25 | 0,212 | 0,000 | 0,756 |  | 0
| 70 | 1,43 | 0,64 | 32 x 4,4 | 3,60 | 1197,04 | 1,52 | 3,05 | 3,539 | 0,000 | 7,851 |  | 0
| 71 | 0,92 | 0,52 | 32 x 4,4 | 0,54 | 811,24 | 1,22 | 0,25 | 0,187 | 0,000 | 0,626 |  | 0
| 72 | 0,35 | 0,27 | 20 x 2,8 | 0,29 | 2543,09 | 1,67 | 3,55 | 4,963 | 0,000 | 5,706 |  | 0
| 72_A | 0,35 | 0,27 | 20 x 2,8 | 2,81 | 2542,95 | 1,67 | 1,90 | 2,656 | 0,000 | 9,809 |  | 0
| 72_B | 0,35 | 0,27 | 20 x 2,8 | 5,21 | 2542,60 | 1,67 | 0,00 | 0,000 | 0,000 | 13,248 |  | 0
| 73 | 0,15 | 0,15 | 16 x 2,2 | 0,95 | 2491,16 | 1,42 | 0,00 | 0,000 | 0,000 | 2,361 |  | 0
| 74 | 0,20 | 0,15 | 16 x 2,2 | 0,82 | 2493,43 | 1,42 | 0,00 | 0,000 | 0,000 | 2,044 |  | 0
| 75 | 0,07 | 0,07 | 16 x 2,2 | 0,85 | 655,62 | 0,66 | 0,00 | 0,000 | 0,000 | 0,556 |  | 0
| 76 | 0,13 | 0,13 | 16 x 2,2 | 1,39 | 1937,65 | 1,23 | 0,00 | 0,000 | 0,000 | 2,698 |  | 0
| 77 | 0,57 | 0,39 | 25 x 3,5 | 0,64 | 1654,98 | 1,53 | 3,00 | 3,524 | 0,000 | 4,588 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 90 -
Project:
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
| 78 | 0,29 | 0,23 | 20 x 2,8 | 1,36 | 1885,60 | 1,41 | 3,55 | 3,533 | 0,000 | 6,104 |  | 0
| 78_A | 0,29 | 0,23 | 20 x 2,8 | 2,69 | 1885,44 | 1,41 | 1,90 | 1,891 | 0,000 | 6,965 |  | 0
| 78_B | 0,29 | 0,23 | 20 x 2,8 | 2,03 | 1885,25 | 1,41 | 0,00 | 0,000 | 0,000 | 3,832 |  | 0
| 79 | 0,22 | 0,17 | 16 x 2,2 | 0,85 | 3104,02 | 1,61 | 0,00 | 0,000 | 0,000 | 2,647 |  | 0
| 80 | 0,07 | 0,07 | 16 x 2,2 | 0,78 | 655,64 | 0,66 | 0,00 | 0,000 | 0,000 | 0,510 |  | 0
| 81 | 0,15 | 0,15 | 16 x 2,2 | 3,05 | 2490,96 | 1,42 | 0,00 | 0,000 | 0,000 | 7,589 |  | 0
| 82 | 0,07 | 0,07 | 16 x 2,2 | 0,66 | 655,67 | 0,66 | 0,00 | 0,000 | 0,000 | 0,432 |  | 0
| 82_A | 0,07 | 0,07 | 16 x 2,2 | 2,71 | 655,53 | 0,66 | 0,00 | 0,000 | 0,000 | 1,776 |  | 0
| 82_B | 0,07 | 0,07 | 16 x 2,2 | 8,54 | 655,09 | 0,66 | 0,00 | 0,000 | 0,000 | 5,595 |  | 0
| 83 | 0,28 | 0,22 | 20 x 2,8 | 0,20 | 1774,89 | 1,36 | 2,20 | 2,044 | 0,000 | 2,401 |  | 0
| 84 | 0,15 | 0,15 | 16 x 2,2 | 0,58 | 2491,86 | 1,42 | 0,00 | 0,000 | 0,000 | 1,448 |  | 0
| 85 | 0,13 | 0,13 | 16 x 2,2 | 1,29 | 1938,27 | 1,23 | 0,00 | 0,000 | 0,000 | 2,498 |  | 0
| 86 | 1,37 | 0,63 | 32 x 4,4 | 3,30 | 1155,16 | 1,49 | 3,55 | 3,956 | 0,000 | 7,768 |  | 0
| 86_A | 1,37 | 0,63 | 32 x 4,4 | 3,60 | 1155,08 | 1,49 | 0,00 | 0,000 | 0,000 | 4,161 |  | 0
| 87 | 0,94 | 0,52 | 32 x 4,4 | 0,54 | 827,77 | 1,24 | 0,25 | 0,191 | 0,000 | 0,639 |  | 0
| 88 | 0,35 | 0,27 | 20 x 2,8 | 4,72 | 2542,71 | 1,67 | 1,65 | 2,307 | 0,000 | 14,296 |  | 0
| 89 | 0,15 | 0,15 | 16 x 2,2 | 0,95 | 2491,29 | 1,42 | 0,00 | 0,000 | 0,000 | 2,362 |  | 0
| 90 | 0,20 | 0,15 | 16 x 2,2 | 0,82 | 2493,56 | 1,42 | 0,00 | 0,000 | 0,000 | 2,044 |  | 0
| 91 | 0,07 | 0,07 | 16 x 2,2 | 0,85 | 655,65 | 0,66 | 0,00 | 0,000 | 0,000 | 0,556 |  | 0
| 92 | 0,13 | 0,13 | 16 x 2,2 | 1,39 | 1937,75 | 1,23 | 0,00 | 0,000 | 0,000 | 2,699 |  | 0
| 93 | 0,59 | 0,40 | 25 x 3,5 | 0,64 | 1720,86 | 1,57 | 2,20 | 2,701 | 0,000 | 3,807 |  | 0
| 94 | 0,21 | 0,16 | 16 x 2,2 | 1,36 | 2797,85 | 1,52 | 0,00 | 0,000 | 0,000 | 3,814 |  | 0
| 94_A | 0,21 | 0,16 | 16 x 2,2 | 0,89 | 2797,69 | 1,52 | 0,00 | 0,000 | 0,000 | 2,494 |  | 0
| 94_B | 0,21 | 0,16 | 16 x 2,2 | 0,23 | 2797,61 | 1,52 | 0,00 | 0,000 | 0,000 | 0,651 |  | 0
| 95 | 0,07 | 0,07 | 16 x 2,2 | 8,31 | 655,40 | 0,66 | 0,00 | 0,000 | 0,000 | 5,446 |  | 0
| 96 | 0,14 | 0,08 | 16 x 2,2 | 0,85 | 803,80 | 0,74 | 0,00 | 0,000 | 0,000 | 0,686 |  | 0
| 97 | 0,07 | 0,07 | 16 x 2,2 | 0,78 | 655,64 | 0,66 | 0,00 | 0,000 | 0,000 | 0,510 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 91 -
Project:
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
| 98 | 0,07 | 0,07 | 16 x 2,2 | 3,05 | 655,55 | 0,66 | 0,00 | 0,000 | 0,000 | 1,997 |  | 0
| 99 | 0,38 | 0,29 | 20 x 2,8 | 0,20 | 2865,35 | 1,79 | 0,00 | 0,000 | 0,000 | 0,576 |  | 0
| 100 | 0,25 | 0,25 | 20 x 2,8 | 0,61 | 2186,60 | 1,54 | 0,00 | 0,000 | 0,000 | 1,325 |  | 0
| 101 | 0,13 | 0,13 | 16 x 2,2 | 1,29 | 1938,13 | 1,23 | 0,00 | 0,000 | 0,000 | 2,498 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 92 -
Project:
Hot water pipe-runs
Pipe-run symbol |  | Sum of normative outputs | Calculation flow | Diameter | Length | Specific friction resistance | Flow velocity | Total friction loss | Pressure drop across fittings | Pressure drop in fittings | Total pressure drop |  | Insulation thickness
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
Source:
| 1 | 0,22 | 0,17 | 16 x 2,2 | 0,50 | 2561,81 | 1,61 | 0,00 | 0,000 | 0,000 | 1,272 |  | 0
| 1 | 0,21 | 0,16 | 16 x 2,2 | 0,47 | 2307,15 | 1,52 | 0,00 | 0,000 | 0,000 | 1,088 |  | 0
| 1 | 0,29 | 0,23 | 20 x 2,8 | 0,52 | 1557,40 | 1,41 | 0,00 | 0,000 | 0,000 | 0,810 |  | 0
| 1 | 0,21 | 0,16 | 16 x 2,2 | 0,52 | 2307,16 | 1,52 | 0,00 | 0,000 | 0,000 | 1,200 |  | 0
| 1 | 0,29 | 0,23 | 20 x 2,8 | 0,47 | 1557,39 | 1,41 | 0,00 | 0,000 | 0,000 | 0,734 |  | 0
| 1 | 0,43 | 0,32 | 20 x 2,8 | 0,50 | 2813,12 | 1,97 | 0,00 | 0,000 | 0,000 | 1,397 |  | 0
| 1 | 0,51 | 0,36 | 25 x 3,5 | 0,59 | 1203,07 | 1,42 | 0,00 | 0,000 | 0,000 | 0,712 |  | 0
| 1 | 0,43 | 0,32 | 20 x 2,8 | 0,59 | 2813,13 | 1,97 | 0,00 | 0,000 | 0,000 | 1,664 |  | 0
| 1_A | 0,22 | 0,17 | 16 x 2,2 | 5,37 | 2562,46 | 1,61 | 0,00 | 0,000 | 0,000 | 13,771 |  | 0
| 2 | 0,14 | 0,08 | 16 x 2,2 | 6,00 | 658,23 | 0,74 | 0,00 | 0,000 | 0,000 | 3,947 |  | 0
| 2 | 0,22 | 0,17 | 16 x 2,2 | 2,53 | 2562,13 | 1,61 | 0,00 | 0,000 | 0,000 | 6,471 |  | 0
| 2 | 0,22 | 0,17 | 16 x 2,2 | 2,21 | 2562,10 | 1,61 | 0,00 | 0,000 | 0,000 | 5,656 |  | 0
| 2 | 0,14 | 0,08 | 16 x 2,2 | 6,21 | 658,25 | 0,74 | 0,00 | 0,000 | 0,000 | 4,089 |  | 0
| 2 | 0,15 | 0,15 | 16 x 2,2 | 0,94 | 2054,19 | 1,42 | 0,00 | 0,000 | 0,000 | 1,936 |  | 0
| 2 | 0,22 | 0,17 | 16 x 2,2 | 0,68 | 2561,90 | 1,61 | 0,00 | 0,000 | 0,000 | 1,738 |  | 0
| 2 | 0,22 | 0,17 | 16 x 2,2 | 0,34 | 2561,88 | 1,61 | 0,00 | 0,000 | 0,000 | 0,859 |  | 0
| 2 | 0,22 | 0,17 | 16 x 2,2 | 5,04 | 2562,39 | 1,61 | 0,00 | 0,000 | 0,000 | 12,904 |  | 0
| 2_A | 0,22 | 0,17 | 16 x 2,2 | 2,82 | 2562,23 | 1,61 | 0,00 | 0,000 | 0,000 | 7,224 |  | 0
| 2_A | 0,22 | 0,17 | 16 x 2,2 | 2,82 | 2562,29 | 1,61 | 0,00 | 0,000 | 0,000 | 7,232 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 93 -
Project:
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
| 2_A | 0,22 | 0,17 | 16 x 2,2 | 1,01 | 2562,46 | 1,61 | 0,00 | 0,000 | 0,000 | 2,580 |  | 0
| 2_A | 0,22 | 0,17 | 16 x 2,2 | 0,93 | 2562,51 | 1,61 | 0,00 | 0,000 | 0,000 | 2,378 |  | 0
| 2_B | 0,22 | 0,17 | 16 x 2,2 | 5,48 | 2563,14 | 1,61 | 0,00 | 0,000 | 0,000 | 14,049 |  | 0
| 2_B | 0,22 | 0,17 | 16 x 2,2 | 6,60 | 2563,29 | 1,61 | 0,00 | 0,000 | 0,000 | 16,911 |  | 0
| 2_B | 0,22 | 0,17 | 16 x 2,2 | 5,47 | 2563,20 | 1,61 | 0,00 | 0,000 | 0,000 | 14,028 |  | 0
| 2_B | 0,22 | 0,17 | 16 x 2,2 | 6,14 | 2563,29 | 1,61 | 0,00 | 0,000 | 0,000 | 15,747 |  | 0
| 3 | 0,15 | 0,15 | 16 x 2,2 | 1,02 | 2054,76 | 1,42 | 0,00 | 0,000 | 0,000 | 2,092 |  | 0
| 3 | 0,07 | 0,07 | 16 x 2,2 | 0,66 | 536,71 | 0,66 | 0,00 | 0,000 | 0,000 | 0,352 |  | 0
| 3 | 0,15 | 0,15 | 16 x 2,2 | 0,94 | 2054,79 | 1,42 | 0,00 | 0,000 | 0,000 | 1,937 |  | 0
| 3 | 0,15 | 0,15 | 16 x 2,2 | 1,02 | 2054,11 | 1,42 | 0,00 | 0,000 | 0,000 | 2,092 |  | 0
| 3 | 0,15 | 0,15 | 16 x 2,2 | 0,66 | 2054,94 | 1,42 | 0,00 | 0,000 | 0,000 | 1,349 |  | 0
| 3 | 0,15 | 0,15 | 16 x 2,2 | 0,56 | 2054,88 | 1,42 | 0,00 | 0,000 | 0,000 | 1,149 |  | 0
| 3 | 0,07 | 0,07 | 16 x 2,2 | 1,66 | 536,37 | 0,66 | 0,00 | 0,000 | 0,000 | 0,888 |  | 0
| 3 | 0,07 | 0,07 | 16 x 2,2 | 0,56 | 536,68 | 0,66 | 0,00 | 0,000 | 0,000 | 0,300 |  | 0
| 4 | 0,07 | 0,07 | 16 x 2,2 | 3,29 | 536,86 | 0,66 | 0,00 | 0,000 | 0,000 | 1,768 |  | 0
| 4 | 0,07 | 0,07 | 16 x 2,2 | 1,66 | 536,54 | 0,66 | 0,00 | 0,000 | 0,000 | 0,888 |  | 0
| 4 | 0,07 | 0,07 | 16 x 2,2 | 0,95 | 536,53 | 0,66 | 0,00 | 0,000 | 0,000 | 0,508 |  | 0
| 4 | 0,07 | 0,07 | 16 x 2,2 | 3,29 | 536,68 | 0,66 | 0,00 | 0,000 | 0,000 | 1,768 |  | 0
| 4 | 0,07 | 0,07 | 16 x 2,2 | 0,95 | 536,70 | 0,66 | 0,00 | 0,000 | 0,000 | 0,508 |  | 0
| 4 | 0,07 | 0,07 | 16 x 2,2 | 1,74 | 536,53 | 0,66 | 0,00 | 0,000 | 0,000 | 0,932 |  | 0
| 4 | 0,07 | 0,07 | 16 x 2,2 | 1,74 | 536,36 | 0,66 | 0,00 | 0,000 | 0,000 | 0,932 |  | 0
| 4_A | 0,07 | 0,07 | 16 x 2,2 | 2,17 | 536,88 | 0,66 | 0,00 | 0,000 | 0,000 | 1,164 |  | 0
| 4_A | 0,07 | 0,07 | 16 x 2,2 | 2,17 | 536,72 | 0,66 | 0,00 | 0,000 | 0,000 | 1,164 |  | 0
| 5 | 0,07 | 0,07 | 16 x 2,2 | 2,04 | 536,14 | 0,66 | 0,00 | 0,000 | 0,000 | 1,094 |  | 0
| 5 | 0,07 | 0,07 | 16 x 2,2 | 1,19 | 536,08 | 0,66 | 0,00 | 0,000 | 0,000 | 0,639 |  | 0
| 5 | 0,29 | 0,23 | 20 x 2,8 | 2,06 | 1557,54 | 1,41 | 1,90 | 1,873 | 0,000 | 5,074 |  | 0
| 5 | 0,21 | 0,16 | 16 x 2,2 | 4,26 | 2307,61 | 1,52 | 0,00 | 0,000 | 0,000 | 9,825 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 94 -
Project:
Pipe-run symbol |  | ΣVR | VS | Diam. | L | R | v | Σζ | Z | Δparm | Δp |  | Insul.
|  | dm³/s | dm³/s | mm | m | Pa/m | m/s |  | kPa | kPa | kPa |  | mm
| 5 | 0,21 | 0,16 | 16 x 2,2 | 2,06 | 2307,39 | 1,52 | 0,00 | 0,000 | 0,000 | 4,742 |  | 0
| 5 | 0,07 | 0,07 | 16 x 2,2 | 2,04 | 536,14 | 0,66 | 0,00 | 0,000 | 0,000 | 1,094 |  | 0
| 5 | 0,07 | 0,07 | 16 x 2,2 | 1,19 | 536,09 | 0,66 | 0,00 | 0,000 | 0,000 | 0,639 |  | 0
| 5_A | 0,21 | 0,16 | 16 x 2,2 | 0,89 | 2307,70 | 1,52 | 0,00 | 0,000 | 0,000 | 2,052 |  | 0
| 5_A | 0,29 | 0,23 | 20 x 2,8 | 2,69 | 1557,81 | 1,41 | 1,90 | 1,873 | 0,000 | 6,063 |  | 0
| 5_B | 0,21 | 0,16 | 16 x 2,2 | 0,19 | 2307,82 | 1,52 | 0,00 | 0,000 | 0,000 | 0,428 |  | 0
| 5_B | 0,29 | 0,23 | 20 x 2,8 | 1,99 | 1558,09 | 1,41 | 0,00 | 0,000 | 0,000 | 3,094 |  | 0
| 6 | 0,07 | 0,07 | 16 x 2,2 | 8,39 | 536,66 | 0,66 | 0,00 | 0,000 | 0,000 | 4,501 |  | 0
| 6 | 0,07 | 0,07 | 16 x 2,2 | 0,60 | 536,26 | 0,66 | 0,00 | 0,000 | 0,000 | 0,321 |  | 0
| 6 | 0,22 | 0,17 | 16 x 2,2 | 0,95 | 2563,25 | 1,61 | 0,00 | 0,000 | 0,000 | 2,447 |  | 0
| 7 | 0,14 | 0,08 | 16 x 2,2 | 0,95 | 658,10 | 0,74 | 0,00 | 0,000 | 0,000 | 0,628 |  | 0
| 7 | 0,14 | 0,08 | 16 x 2,2 | 2,40 | 658,26 | 0,74 | 0,00 | 0,000 | 0,000 | 1,580 |  | 0
| 7 | 0,07 | 0,07 | 16 x 2,2 | 0,73 | 536,39 | 0,66 | 0,00 | 0,000 | 0,000 | 0,391 |  | 0
| 8 | 0,07 | 0,07 | 16 x 2,2 | 0,78 | 536,52 | 0,66 | 0,00 | 0,000 | 0,000 | 0,419 |  | 0
| 8 | 0,07 | 0,07 | 16 x 2,2 | 0,73 | 536,32 | 0,66 | 0,00 | 0,000 | 0,000 | 0,391 |  | 0
| 8 | 0,15 | 0,15 | 16 x 2,2 | 2,93 | 2054,63 | 1,42 | 0,00 | 0,000 | 0,000 | 6,015 |  | 0
| 9 | 0,07 | 0,07 | 16 x 2,2 | 1,45 | 536,56 | 0,66 | 0,00 | 0,000 | 0,000 | 0,780 |  | 0
| 9 | 0,07 | 0,07 | 16 x 2,2 | 0,79 | 536,34 | 0,66 | 0,00 | 0,000 | 0,000 | 0,425 |  | 0
| 9 | 0,07 | 0,07 | 16 x 2,2 | 2,93 | 536,44 | 0,66 | 0,00 | 0,000 | 0,000 | 1,570 |  | 0
| 9_A | 0,07 | 0,07 | 16 x 2,2 | 2,70 | 536,55 | 0,66 | 0,00 | 0,000 | 0,000 | 1,451 |  | 0
| 9_A | 0,07 | 0,07 | 16 x 2,2 | 2,78 | 536,81 | 0,66 | 0,00 | 0,000 | 0,000 | 1,494 |  | 0
| 9_B | 0,07 | 0,07 | 16 x 2,2 | 8,49 | 537,20 | 0,66 | 0,00 | 0,000 | 0,000 | 4,561 |  | 0
| 9_B | 0,07 | 0,07 | 16 x 2,2 | 6,69 | 537,36 | 0,66 | 0,00 | 0,000 | 0,000 | 3,593 |  | 0
| 9_C | 0,07 | 0,07 | 16 x 2,2 | 1,93 | 537,86 | 0,66 | 0,00 | 0,000 | 0,000 | 1,040 |  | 0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [11 empty] | - 95 -

## Receptor
Project:
Receptor
Receptors |  | Type | VR | VC | preq | Δphydr | Δproute | Δpsurplus |  | θinlet
|  |  | dm³/s | dm³/s | kPa | kPa | kPa | kPa |  | °C
Source:
Available pressure CW: 319,004 kPa
| 116_WbA | CW | 0,070 | 0,000 | 100,000 | 26,431 | -250,429 | 122,108 |  | 10,13
| 116_WbA | HW | 0,070 | 0,000 | 100,000 | 26,431 | -189,853 | 58,526 |  | 44,66
| 115_WbA | CW | 0,070 | 0,000 | 100,000 | 26,431 | -242,446 | 114,125 |  | 10,15
| 115_WbA | HW | 0,070 | 0,000 | 100,000 | 26,431 | -179,470 | 48,143 |  | 44,64
| 111_WbA | CW | 0,070 | 0,000 | 100,000 | 26,431 | -260,611 | 133,293 |  | 10,08
| 111_WbA | HW | 0,070 | 0,000 | 100,000 | 26,431 | -140,313 | 9,267 |  | 44,74
| 112_WbA | CW | 0,070 | 0,000 | 100,000 | 26,431 | -241,507 | 114,224 |  | 10,10
| 112_WbA | HW | 0,070 | 0,000 | 100,000 | 26,431 | -162,585 | 29,447 |  | 44,74
| 109_WbA | CW | 0,070 | 0,000 | 100,000 | 26,431 | -267,327 | 140,009 |  | 10,08
| 109_WbA | HW | 0,070 | 0,000 | 100,000 | 26,431 | -146,310 | 15,263 |  | 44,82
| 116_WCB | CW | 0,130 | 0,000 | 50,000 | 21,725 | -262,262 | 188,647 |  | 10,06
| 115_WCB | CW | 0,130 | 0,000 | 50,000 | 21,725 | -252,045 | 178,430 |  | 10,08
| 112_WCB | CW | 0,130 | 0,000 | 50,000 | 21,725 | -240,427 | 167,850 |  | 10,10
| 111_WCB | CW | 0,130 | 0,000 | 50,000 | 21,725 | -258,469 | 185,856 |  | 10,08
| 109_WCB | CW | 0,130 | 0,000 | 50,000 | 21,725 | -282,488 | 209,875 |  | 10,04
| 116_BtC | CW | 0,150 | 0,000 | 100,000 | 24,480 | -250,992 | 124,622 |  | 10,08
| 116_BtC | HW | 0,150 | 0,000 | 100,000 | 24,480 | -190,377 | 61,001 |  | 44,79
| 115_BtC | CW | 0,150 | 0,000 | 100,000 | 24,480 | -243,111 | 116,741 |  | 10,10
| 115_BtC | HW | 0,150 | 0,000 | 100,000 | 24,480 | -179,889 | 50,513 |  | 44,78
| 109_BtC | CW | 0,150 | 0,000 | 100,000 | 24,480 | -260,249 | 134,881 |  | 10,09
| 109_BtC | HW | 0,150 | 0,000 | 100,000 | 24,480 | -140,686 | 11,591 |  | 44,79
| 111_TrayC | CW | 0,150 | 0,000 | 100,000 | 30,009 | -260,849 | 129,953 |  | 10,07
| 111_TrayC | HW | 0,150 | 0,000 | 100,000 | 30,009 | -139,154 | 4,529 |  | 44,80
| 112_TrayC | CW | 0,150 | 0,000 | 100,000 | 30,009 | -241,922 | 111,060 |  | 10,09
| 112_TrayC | HW | 0,150 | 0,000 | 100,000 | 30,009 | -161,536 | 24,820 |  | 44,80
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [8 empty] | - 96 -
Project:
Receptor
Receptors |  | Type | VR | VC | preq | Δphydr | Δproute | Δpsurplus |  | θinlet
|  |  | dm³/s | dm³/s | kPa | kPa | kPa | kPa |  | °C
| 115_D | CW | 0,150 | 0,000 | 50,000 | 19,764 | -254,363 | 182,709 |  | 10,08
| 109_D | CW | 0,150 | 0,000 | 50,000 | 19,764 | -283,537 | 212,886 |  | 10,03
| 116_D | CW | 0,150 | 0,000 | 50,000 | 19,764 | -263,912 | 192,257 |  | 10,06
| 103_SinkA | CW | 0,070 | 0,000 | 100,000 | 24,519 | -266,286 | 139,876 |  | 10,08
| 103_SinkA | HW | 0,070 | 0,000 | 100,000 | 24,519 | -205,291 | 75,875 |  | 44,89
| 106_SinkA | CW | 0,070 | 0,000 | 100,000 | 24,519 | -276,206 | 149,797 |  | 10,05
| 106_SinkA | HW | 0,070 | 0,000 | 100,000 | 24,519 | -215,484 | 86,068 |  | 44,94
| 104_SinkA | CW | 0,070 | 0,000 | 100,000 | 24,519 | -262,681 | 137,275 |  | 10,25
| 104_SinkA | HW | 0,070 | 0,000 | 100,000 | 24,519 | -142,711 | 13,576 |  | 44,31
| 216_WbA | CW | 0,070 | 0,000 | 100,000 | 58,783 | -259,475 | 100,363 |  | 10,15
| 216_WbA | HW | 0,070 | 0,000 | 100,000 | 58,783 | -224,260 | 65,110 |  | 44,59
| 215_WbA | CW | 0,070 | 0,000 | 100,000 | 58,783 | -250,091 | 90,978 |  | 10,17
| 215_WbA | HW | 0,070 | 0,000 | 100,000 | 58,783 | -214,250 | 55,101 |  | 44,57
| 211_WbA | CW | 0,070 | 0,000 | 100,000 | 58,783 | -271,994 | 112,359 |  | 10,08
| 211_WbA | HW | 0,070 | 0,000 | 100,000 | 58,783 | -170,228 | 4,738 |  | 44,81
| 212_WbA | CW | 0,070 | 0,000 | 100,000 | 58,783 | -249,419 | 90,416 |  | 10,10
| 212_WbA | HW | 0,070 | 0,000 | 100,000 | 58,783 | -215,172 | 56,128 |  | 44,81
| 209_WbA | CW | 0,070 | 0,000 | 100,000 | 58,783 | -276,928 | 117,293 |  | 10,08
| 209_WbA | HW | 0,070 | 0,000 | 100,000 | 58,783 | -175,822 | 10,332 |  | 44,85
| 216_WCB | CW | 0,130 | 0,000 | 50,000 | 54,077 | -263,365 | 158,958 |  | 10,06
| 215_WCB | CW | 0,130 | 0,000 | 50,000 | 54,077 | -253,375 | 148,968 |  | 10,08
| 212_WCB | CW | 0,130 | 0,000 | 50,000 | 54,077 | -248,339 | 144,043 |  | 10,10
| 211_WCB | CW | 0,130 | 0,000 | 50,000 | 54,077 | -269,851 | 164,922 |  | 10,07
| 209_WCB | CW | 0,130 | 0,000 | 50,000 | 54,077 | -282,010 | 177,080 |  | 10,05
| 216_BtC | CW | 0,070 | 0,000 | 100,000 | 56,832 | -261,205 | 104,043 |  | 10,11
| 216_BtC | HW | 0,070 | 0,000 | 100,000 | 56,832 | -225,633 | 68,434 |  | 44,71
| 215_BtC | CW | 0,070 | 0,000 | 100,000 | 56,832 | -251,776 | 94,614 |  | 10,12
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [8 empty] | - 97 -
Project:
Receptor
Receptors |  | Type | VR | VC | preq | Δphydr | Δproute | Δpsurplus |  | θinlet
|  |  | dm³/s | dm³/s | kPa | kPa | kPa | kPa |  | °C
| 215_BtC | HW | 0,070 | 0,000 | 100,000 | 56,832 | -215,666 | 58,467 |  | 44,70
| 209_BtC | CW | 0,070 | 0,000 | 100,000 | 56,832 | -275,442 | 117,757 |  | 10,11
| 209_BtC | HW | 0,070 | 0,000 | 100,000 | 56,832 | -174,643 | 11,104 |  | 44,75
| 211_TrayC | CW | 0,150 | 0,000 | 100,000 | 62,361 | -272,232 | 109,019 |  | 10,06
| 211_TrayC | HW | 0,150 | 0,000 | 100,000 | 62,361 | -169,069 | 0,000 |  | 44,87
| 212_TrayC | CW | 0,150 | 0,000 | 100,000 | 62,361 | -249,833 | 87,253 |  | 10,09
| 212_TrayC | HW | 0,150 | 0,000 | 100,000 | 62,361 | -214,123 | 51,501 |  | 44,86
| 215_WMD | CW | 0,250 | 0,000 | 100,000 | 52,117 | -254,850 | 102,404 |  | 10,07
| 209_WMD | CW | 0,250 | 0,000 | 100,000 | 52,117 | -283,182 | 130,213 |  | 10,04
| 216_WMD | CW | 0,250 | 0,000 | 100,000 | 52,117 | -264,406 | 111,960 |  | 10,05
| 203_SinkA | CW | 0,070 | 0,000 | 100,000 | 56,871 | -260,742 | 103,541 |  | 10,09
| 203_SinkA | HW | 0,070 | 0,000 | 100,000 | 56,871 | -219,013 | 61,775 |  | 44,89
| 206_SinkA | CW | 0,070 | 0,000 | 100,000 | 56,871 | -270,660 | 113,458 |  | 10,06
| 206_SinkA | HW | 0,070 | 0,000 | 100,000 | 56,871 | -229,242 | 72,004 |  | 44,93
| 204_SinkA | CW | 0,070 | 0,000 | 100,000 | 56,871 | -272,678 | 114,954 |  | 10,19
| 204_SinkA | HW | 0,070 | 0,000 | 100,000 | 56,871 | -172,341 | 8,763 |  | 44,53
| 101_SinkA | CW | 0,070 | 0,000 | 100,000 | 24,519 | -247,480 | 122,108 |  | 10,31
| 101_SinkA | HW | 0,070 | 0,000 | 100,000 | 24,519 | -168,161 | 36,934 |  | 44,20
| 108_WMA | CW | 0,250 | 0,000 | 100,000 | 19,764 | -266,572 | 145,956 |  | 10,05
| 108_WCB | CW | 0,130 | 0,000 | 50,000 | 21,725 | -264,062 | 191,485 |  | 10,05
| 108_BtC | CW | 0,070 | 0,000 | 100,000 | 24,480 | -257,551 | 132,219 |  | 10,07
| 108_BtC | HW | 0,070 | 0,000 | 100,000 | 24,480 | -176,327 | 45,140 |  | 44,88
| 108_WbD | CW | 0,070 | 0,000 | 100,000 | 26,431 | -255,574 | 128,291 |  | 10,11
| 108_WbD | HW | 0,070 | 0,000 | 100,000 | 26,431 | -174,648 | 41,510 |  | 44,77
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [8 empty] | - 98 -

## Critical hydraulic routes
Project:
Critical hydraulic routes
## |  | Name |  | Description | Unit | CW |  | HW
Source: |  |  | no name
|  | Critical path symbol |  |  |  | 211_TrayC HW
| 1 | Required pressure in source |  | pminR | kPa | 319,004
| 2 | Hydrostatic head |  | Δphyd | kPa | 62,361
| 3 | Pressure drop on devices |  |  | kPa
|  | Water meter |  | ΔpWM | kPa
|  | Filter |  | ΔpFIL | kPa
|  | Heater |  | ΔpHT | kPa | 105,455
|  | Regulator/reductor |  | ΔpREG | kPa
|  | Remaining devices |  | ΔpRST | kPa
| 4 | Minimum pressure at supply point |  | Δpmin rec | kPa | 100,000
| 5 | Pressure boosting device |  | Δppump | kPa
| 6 | Total pressure drop (no.2) to (no.4) |  | ΣΔp | kPa | 267,816
| 7 | Remaining pressure drop for local drops and along pipe length. Calculated as (no.1) - (no.6) + (no.5) |  | Δprst | kPa | 51,187
| 8 | Contribution from local drops |  |  | kPa | 22,860
| 9 | Remaining pressure drop along pipe length. Calculated as (no.7) - (no.8) |  |  | kPa | 28,327
| 10 | Critical path length |  | L | m | 17,02
| 11 | Available value of linear friction resistance. Calculated as (no.9)/(no.10) |  | Ravail | Pa/m | 1664,38
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 99 -

## Flow paths HW
Project:
Flow paths HW
Pipe-run symbol |  | Type | L | ΣVR | VS | Diam. | v |  | R | R*L | Σζ | Z | Δparm |  | Δp |  | Δθ
|  |  | m | dm³/s | dm³/s | mm | m/s |  | Pa/m | kPa |  | kPa | kPa |  | kPa |  | K
Source: no name
Path to receptor: 211_TrayC Type: HW
| no name | SRC |  | 8,060 | 1,260 | [9 empty] | -319,00
| 1 | CW | 1,96 | 8,060 | 1,260 | 40 x 5,5 | 1,908 |  | 1355,52 | 2,65 | 4,05 | 7,37 | 0,00 |  | 10,02 |  | 0,0
| 69 | CW | 0,73 | 2,800 | 0,860 | 40 x 5,5 | 1,302 |  | 688,46 | 0,50 | 5,45 | 4,62 | 0,00 |  | 5,12 |  | 0,0
| 69_A | CW | 0,79 | 2,800 | 0,860 | 40 x 5,5 | 1,302 |  | 688,45 | 0,54 | 0,25 | 0,21 | 0,00 |  | 0,76 |  | 0,0
| 86 | CW | 3,30 | 1,370 | 0,631 | 32 x 4,4 | 1,493 |  | 1155,16 | 3,81 | 3,55 | 3,96 | 0,00 |  | 7,77 |  | 0,0
| 86_A | CW | 3,60 | 1,370 | 0,631 | 32 x 4,4 | 1,493 |  | 1155,08 | 4,16 | 0,00 | 0,00 | 0,00 |  | 4,16 |  | 0,0
| no name | FS |  | 0,430 | 0,321 | [9 empty] | 105,45
| 1 | HW | 0,59 | 0,430 | 0,321 | 20 x 2,8 | 1,969 |  | 2813,13 | 1,66 | 0,00 | 0,00 | 0,00 |  | 1,66 |  | 0,0
| 2 | HW | 5,04 | 0,220 | 0,170 | 16 x 2,2 | 1,609 |  | 2562,39 | 12,90 | 0,00 | 0,00 | 0,00 |  | 12,90 |  | 0,1
| 3 | HW | 1,02 | 0,150 | 0,150 | 16 x 2,2 | 1,419 |  | 2054,11 | 2,09 | 0,00 | 0,00 | 0,00 |  | 2,09 |  | 0,0
| 211_TrayC | HW |  | 0,150 | 0,150 |  | 0,000 |  |  |  | 0,00 |  |  |  | 0,00
[8 empty] | ΣΔp = | [7 empty] | -169,07 |  | kPa
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [13 empty] | - 100 -

## Component list on CW pipe-r
Project:
Component list on CW pipe-runs
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 1, Source: , m= 4535 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 2,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 2,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  |  |  | 0,0
Pipe-run (CW) 2, Source: , m= 3919 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  |  |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  | 2,8 |  | 3,8
Pipe-run (CW) 3, Source: , m= 2482 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 1,9
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  | 2,8 |  | 3,7
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 101 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 3_A, Source: , m= 2482 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  | 0,0
Pipe-run (CW) 4, Source: , m= 1793 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 1,1
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2,8 |  | 5,4
Pipe-run (CW) 5, Source: , m= 1404 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
Pipe-run (CW) 6, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 7, Source: , m= 1286 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,2
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 102 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 7_A, Source: , m= 1286 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,2
Pipe-run (CW) 7_B, Source: , m= 1286 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
Pipe-run (CW) 8, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 9, Source: , m= 980 kg/h
Pipe-run (CW) 10, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 11, Source: , m= 612 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 12, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 103 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
m³/h
Pipe-run (CW) 13, Source: , m= 252 kg/h
Pipe-run (CW) 13_A, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 14, Source: , m= 1722 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 1,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 2,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1,4 |  | 2,5
Pipe-run (CW) 14_A, Source: , m= 1722 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
Pipe-run (CW) 15, Source: , m= 1435 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 104 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 16, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 17, Source: , m= 1321 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,6
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  |  |  | 0,0
Pipe-run (CW) 18, Source: , m= 900 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  | 1,4 |  | 1,6
Pipe-run (CW) 19, Source: , m= 770 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  | 1,4 |  | 1,2
Pipe-run (CW) 20, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 105 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 21, Source: , m= 283 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 22, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 23, Source: , m= 252 kg/h
Pipe-run (CW) 23_A, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 24, Source: , m= 3411 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  |  |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  | 1,4 |  | 1,4
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 106 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 25, Source: , m= 2482 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 1,9
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  | 2,8 |  | 3,7
Pipe-run (CW) 25_A, Source: , m= 2482 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  | 0,0
Pipe-run (CW) 26, Source: , m= 1793 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 1,1
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2,8 |  | 5,4
Pipe-run (CW) 27, Source: , m= 1404 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 107 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 28, Source: , m= 1286 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,2
Pipe-run (CW) 28_A, Source: , m= 1286 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,2
Pipe-run (CW) 28_B, Source: , m= 1286 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
Pipe-run (CW) 29, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 30, Source: , m= 980 kg/h
Pipe-run (CW) 31, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 108 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 32, Source: , m= 612 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 33, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 34, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 35, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 36, Source: , m= 1722 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 1,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 2,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1,4 |  | 2,5
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 109 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 36_A, Source: , m= 1722 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
Pipe-run (CW) 37, Source: , m= 1435 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
Pipe-run (CW) 38, Source: , m= 1321 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,6
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  |  |  | 0,0
Pipe-run (CW) 39, Source: , m= 900 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  | 1,4 |  | 1,6
Pipe-run (CW) 40, Source: , m= 770 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  | 1,4 |  | 1,2
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 110 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 41, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 42, Source: , m= 283 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 43, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 44, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 45, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 111 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 46, Source: , m= 2658 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 2,1
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  | 1,4 |  | 2,1
Pipe-run (CW) 46_A, Source: , m= 2658 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 2,1
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,4
Pipe-run (CW) 46_B, Source: , m= 2658 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1"MT |  | 0,3 |  | 0,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  |  |  | 0,0
Pipe-run (CW) 47, Source: , m= 2272 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 32 - 32 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 2,8 |  | 3,1
Pipe-run (CW) 48, Source: , m= 1881 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 32 - 32 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1"MT |  | 0,3 |  | 0,2
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  |  |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 112 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 49, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 2,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  | 1,4 |  | 2,0
Pipe-run (CW) 49_A, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 2,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
Pipe-run (CW) 49_B, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (CW) 50, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 51, Source: , m= 540 kg/h
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 113 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 52, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 53, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 54, Source: , m= 1435 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  |  |  | 0,0
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  | 1,4 |  | 1,7
Pipe-run (CW) 55, Source: , m= 900 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  | 1,4 |  | 1,6
Pipe-run (CW) 56, Source: , m= 956 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  | 1,4 |  | 1,9
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 114 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 57, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 58, Source: , m= 577 kg/h
Pipe-run (CW) 58_A, Source: , m= 577 kg/h
Pipe-run (CW) 59, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 60, Source: , m= 283 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 61, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 62, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 115 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 62_A, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 62_B, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 62_C, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 63, Source: , m= 1404 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,6
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,6
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1"FT - 1"FT - 1"FT |  | 1,4 |  | 1,6
Pipe-run (CW) 63_A, Source: , m= 1404 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 116 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 64, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 2,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
Pipe-run (CW) 64_A, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (CW) 65, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 66, Source: , m= 540 kg/h
Pipe-run (CW) 67, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 68, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 117 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 69, Source: , m= 3094 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 1,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 1,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  | 1,4 |  | 1,2
Pipe-run (CW) 69_A, Source: , m= 3094 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 40 - 1¼"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  |  |  | 0,0
Pipe-run (CW) 70, Source: , m= 2318 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 32 - 32 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 32 - 32 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  | 2,8 |  | 3,2
Pipe-run (CW) 71, Source: , m= 1860 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 32 - 32 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1"MT |  | 0,3 |  | 0,2
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  |  |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 118 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 72, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 2,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  | 1,4 |  | 2,0
Pipe-run (CW) 72_A, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 2,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
Pipe-run (CW) 72_B, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (CW) 73, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 74, Source: , m= 540 kg/h
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 119 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 75, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 76, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 77, Source: , m= 1404 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,6
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,6
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  |  |  | 0,0
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  | 1,4 |  | 1,6
Pipe-run (CW) 78, Source: , m= 827 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  | 1,4 |  | 1,4
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 120 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 78_A, Source: , m= 827 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
Pipe-run (CW) 78_B, Source: , m= 827 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (CW) 79, Source: , m= 612 kg/h
Pipe-run (CW) 80, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 81, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 82, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 121 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 82_A, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 82_B, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 83, Source: , m= 799 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,5
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| Brass and steel pipe couplings and fittings | Tee 1"FT - ¾"FT - 1"FT |  | 1,4 |  | 1,3
Pipe-run (CW) 84, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 85, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 122 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 86, Source: , m= 2272 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow 1¼"FT |  | 1,4 |  | 1,6
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1¼"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Tee 1¼"FT - 1¼"FT - 1¼"FT |  | 1,4 |  | 1,6
Pipe-run (CW) 86_A, Source: , m= 2272 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 32 - 32 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 32 - 32 |  | 0,0 |  | 0,0
Pipe-run (CW) 87, Source: , m= 1881 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 32 - 32 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 32 - 1"MT |  | 0,3 |  | 0,2
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  |  |  | 0,0
Pipe-run (CW) 88, Source: , m= 980 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,3
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  | 1,4 |  | 2,0
Pipe-run (CW) 89, Source: , m= 540 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 123 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
m³/h
Pipe-run (CW) 90, Source: , m= 540 kg/h
Pipe-run (CW) 91, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 92, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 93, Source: , m= 1435 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Reduction fitting FT-MT 1"MT - ¾"FT |  | 0,6 |  | 0,7
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 25 - ¾"MT |  | 0,3 |  | 0,3
| Brass and steel pipe couplings and fittings | Tee 1"FT - 1"FT - ¾"FT |  | 1,4 |  | 1,7
Pipe-run (CW) 94, Source: , m= 577 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 94_A, Source: , m= 577 kg/h
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 124 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
m³/h
Pipe-run (CW) 94_B, Source: , m= 577 kg/h
Pipe-run (CW) 95, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 96, Source: , m= 283 kg/h
Pipe-run (CW) 97, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 98, Source: , m= 252 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (CW) 99, Source: , m= 1049 kg/h
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 125 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (CW) 100, Source: , m= 900 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (CW) 101, Source: , m= 468 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 126 -
Project:
Component list on HW pipe-runs
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 1, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 1, Source: , m= 571 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 1, Source: , m= 819 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (HW) 1, Source: , m= 571 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 1, Source: , m= 819 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (HW) 1, Source: , m= 1143 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (HW) 1, Source: , m= 1291 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 25 - 25 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 127 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 1, Source: , m= 1143 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (HW) 1_A, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2, Source: , m= 280 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2, Source: , m= 280 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2, Source: , m= 606 kg/h
Pipe-run (HW) 2, Source: , m= 535 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 128 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 2, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2_A, Source: , m= 606 kg/h
Pipe-run (HW) 2_A, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2_A, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2_A, Source: , m= 606 kg/h
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 129 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 2_B, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2_B, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2_B, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 2_B, Source: , m= 606 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 3, Source: , m= 535 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 3, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 130 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 3, Source: , m= 535 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 3, Source: , m= 535 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 3, Source: , m= 535 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 3, Source: , m= 535 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 3, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 3, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 4, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 131 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 4, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 4, Source: , m= 250 kg/h
Pipe-run (HW) 4, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 4, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 4, Source: , m= 250 kg/h
Pipe-run (HW) 4, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 132 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 4_A, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 4_A, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 5, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 5, Source: , m= 571 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 5, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 5, Source: , m= 571 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 133 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 5, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 5, Source: , m= 819 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
Pipe-run (HW) 5, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 5_A, Source: , m= 571 kg/h
Pipe-run (HW) 5_A, Source: , m= 819 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
| PEX (pipes and fittings) acc. to EN ISO 15875 | Elbow ¾"FT |  | 1,4 |  | 1,4
| PEX (pipes and fittings) acc. to EN ISO 15875 | Fitting with male thread PN10 20 - ¾"MT |  | 0,3 |  | 0,2
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 134 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
m³/h
Pipe-run (HW) 5_B, Source: , m= 571 kg/h
Pipe-run (HW) 5_B, Source: , m= 819 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 20 - 20 |  | 0,0 |  | 0,0
Pipe-run (HW) 6, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 6, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 6, Source: , m= 606 kg/h
Pipe-run (HW) 7, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 135 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
m³/h
Pipe-run (HW) 7, Source: , m= 280 kg/h
Pipe-run (HW) 7, Source: , m= 280 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 8, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 8, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 8, Source: , m= 535 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 9, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 136 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 9, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 9, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 9_A, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 9_A, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 9_B, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
Pipe-run (HW) 9_B, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 137 -
Project:
Catalogue |  | Component name | Catalogue code | ζ | kv | Pressure drop
[5 empty] | m³/h | kPa
Pipe-run (HW) 9_C, Source: , m= 250 kg/h
| PEX (pipes and fittings) acc. to EN ISO 15875 | Bend support 16 - 16 |  | 0,0 |  | 0,0
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 | [6 empty] | - 138 -

## List of pipes, pipe fitting-1
Project:
List of pipes, pipe fittings and couplings
Product |  | Size | Catalogue code |  | Qty. | Unit
Brass and steel pipe couplings and fittings
Pipe fittings
| Female connector, reduction, imperial | 1"FT - ¾"FT |  |  | 10 | pcs.
| Tee | 1"FT - ¾"FT - 1"FT |  |  | 12 | pcs.
| Tee | 1"FT - 1"FT - ¾"FT |  |  | 21 | pcs.
PEX (pipes and fittings) acc. to EN ISO 15875
Pipes
| Pipe PN10 in coils | 16 x 2,2 |  |  | 254 | m
| Pipe PN10 in coils | 20 x 2,8 |  |  | 50 | m
| Pipe PN10 in coils | 25 x 3,5 |  |  | 33 | m
| Pipe PN10 in coils | 32 x 4,4 |  |  | 24 | m
| Pipe PN10 in coils | 40 x 5,5 |  |  | 16 | m
Pipe fittings
| Bend support | 16 - 16 |  |  | 183 | pcs.
| Bend support | 20 - 20 |  |  | 26 | pcs.
| Bend support | 25 - 25 |  |  | 16 | pcs.
| Bend support | 32 - 32 |  |  | 8 | pcs.
| Elbow | ¾"FT |  |  | 16 | pcs.
| Elbow | 1¼"FT |  |  | 9 | pcs.
| Fitting with male thread PN10 | 20 - ¾"MT |  |  | 41 | pcs.
| Fitting with male thread PN10 | 25 - ¾"MT |  |  | 33 | pcs.
| Fitting with male thread PN10 | 32 - 1"MT |  |  | 13 | pcs.
| Fitting with male thread PN10 | 32 - 1¼"MT |  |  | 15 | pcs.
| Fitting with male thread PN10 | 40 - 1¼"MT |  |  | 15 | pcs.
| Reduction fitting FT-MT | 1"MT - ¾"FT |  |  | 21 | pcs.
| Tee | 1"FT - 1"FT - 1"FT |  |  | 12 | pcs.
| Tee | 1¼"FT - 1¼"FT - 1¼"FT |  |  | 12 | pcs.
InstalSystem 5 EN (Rev. 17.0) © InstalSoft 1996-2019 |  |  |  | - 139 -